SPEECON 7200M3

Manual

27/03/03

PART I 7200M3 MAIN UNIT

CONTENTS                    Page

7200M3 INVERTER MAIN UNIT

5

5

6

7

8

8

9

11

17

20

20

21

23

25

27

27

28

28

31

30

30

34

35

37

37

44

46

1

1.1 PARTS NAMES OF 7200M3

1.2 RECEIVING

  - INSTALLATION

1.4 WIRING

1.4.1 Terminal Cover Mounting/Removing

1.4.2 Standard Wiring Diagram

1.4.3 Main Circuit

1.4.4 Control Circuit

1.5 OPERATION

1.5.1 Pre-operation Check

1.5.2 Pre-operation Setting

1.5.3 Test Run Method

1.5.4 Inverter Status Display LED

1.5.5 Digital Operator Display

1.5.6 Check Points at Test Run

1.6 MAINTENANCE

1.6.1 Periodical Inspection

1.6.2 High Voltage Test

1.7 FAULT DISPLAY AND TROUBLESHOOTING

1.7.1 Checking of Causes

1.7.2 Alarm Display and Contents

1.7.3 Corrective Action for Motor Faults

1.8 SPECIFICATIONS

1.8.1 Specifications

1.8.2 Dimensions

  - OPTIONS AND PERIPHERAL UNITS

PART II 7200M3 MAIN UNIT

##### CONTENTS                         Page

47

48

48

50

52

53

55

55

56

57

57

59

60

62

62

65

68

71

71

72

73

74

76

77

78

80

81

2. DESCRIPTION OF DIGITAL OPERATING SECTION

2.1 FUNCTION/CONSTANT SETTING

2.1.1 DRV (Drive) Mode and PRG (Program) Mode

2.1.2 Constant Reading and Setting

2.1.3 Precautions on Constant Setting

2.2 DIGITAL OPERATOR OPERATION EXAMPLE

2.3 CONSTANT INITIALIZATION AND LOCK PROTECTION

2.3.1 Constant Initialization

2.3.2 Constant Lock Protection

2.4 CORRECTIVE FUNCTION

2.4.1 Output Frequency Bias (Pn-23) and Gain (Pn-22)

2.4.2 Calibration of Frequency Meter

2.5 MONITOR FUNCTION

2.6 FUNCTION/CONSTANT LIST

2.6.1 A Group Functions(Constant Pn-00 to 19)

2.6.2 B Group Functions(Constant Pn-20 to 29)

2.6.3 C Group Functions (Constant Pn-30 to 59)

2.7 DESCRIPTION OF FUNCTIONS AND CONSTANTS

2.7.1 Display of Operator

2.7.2 Run/Stop Procedure Selection

2.7.3 V/f Characteristic Setting

2.7.4 Accel / Decel Time Setting

2.7.5 4-Step Speed Change

2.7.6 Jog Operation

2.7.7 Electronic Thermal Overload Function

2.7.8 Multifunction Analog Output Monitor Setting

PART II 7200M3 MAIN UNIT

CONTENTS                    Page

2.7.9 S-Curve Pattern Selection

81

82

83

84

85

86

88

90

91

92

93

94

95

97

99

100

102

104

105

107

2.7.10 Frequency Command GAIN/BIAS

2.7.11 Output Frequency Limit

2.7.12 DC Injection Braking

2.7.13 FULL-RANGE AUTOMATIC TORQUE BOOST

2.7.14 MOTOR STALL PREVENTION FUNCTION

2.7.15 ULTIFUNCTION CONTACT INPUT FUNCTION SELECTION

2.7.16 MULTIFUNCTION PHOTO- COUPLER OUTPUT FUNCTION

2.7.17 SPEED AGREED SIGNAL OUTPUT

2.7.18 OVERTORQUE DETECTION FUNCTION

2.7.19 CARRIER FREQUENCY SETTING

2.7.20 FREQUENCY/CURRENT METER CALIBRATION

2.7.21 OPERATION AT MOMENTARY POWER LOSS

2.7.22 AUTOMATIC RESET AND RESTART FUNCTION

2.7.23 FREQUENCY JUMP CONTROL

2.7.24 SPEED SEARCH FUNCTION

2.7.25 FREQUENCY UP/ DOWN FUNCTION

2.7.26 FUNCTIONS FOR REDUCTION OF MACHINE

2.8 PROTECTION FUNCTION AND TROUBLESHOOTING

2.9 Warning and Self-Diagnosis Functions

1 7200M3 INVERTER MAIN UNIT

The 7200M3 is an all-digital inverter of compact size and low noise. Two types of models are available: with digital operator (JNEP--13) and with analog operator (JNEP--14). Using the digital operator achieves optimum drive and monitoring by changing the control constant setting. The model provided with the analog operator is used for simple applications where no complicated constant setting are necessary. Free kit operator (JNEP--15) is also available for sample applications.

  - PARTS NAMES OF 7200M3

• With Digital operator

PROTECTIVE COVER

TERMINAL COVER

DIGITAL OPERATOR (JNEP--13

DIE-CAST CASE

• With analog operator                     • Free Kit operator

External dimensions and mounting            Dimensions are the same as

Method of analog operator is                As for digital operator.

the same as for digital operator.

ANALOG OPERATOR (JNEP--14)

  - RECEIVING

This 7200M3 has been put thorough demanding tests at the factory before shipment.

After unpacking, check for the following.

˙Verify the part numbers with the purchase order sheet and/or packing slip.

˙Transit damage

If any part of 7200M3 is damaged or missing, immediately notify the shipper.

# NAMEPLATE DATA

INVERTER MODEL

INPUT SPEC.

OUTPUT SPEC.

SERIES NUMBER

| MODEL INPUT OUTPUT SER.NO. | ###### JNTABDCB0001JK--- 220V CLASS INVERTER AC 3PH 200-230 50/60Hz AC 3PH 0-230V 2KVA 5A |
| --- | --- |
| TECO ELEC. & MACH. CO., LTD. 3H045D1160003 |  |

MODEL DESIGNATION

JNT  A  BD  B  B  0001  JK  ---

7200M3 SERIES                                              Reserved

Voltage

Input Voltage                                            JK:200 to 230V

A:Three-phase                                            AZ:400 to 460V

B:Single-phase

Specifications                                Applicable max. motor Output

BD:Domestic standards                           R500:0.5HP

BE:UL listed component

(planning)                                      0010:10HP

Operator type                               Enclosures and mountings

B:Digital Operator (JNEP--13)                  A:Open chassis type (IEC IP00)

C:Analog Operator (JNEP--14)                 B:Enclosed ,Wall-mounted type

D:Free Kit (JNEP--15)                        (NEMA-1)

  - INSTALLATION

CAUTION:

• Handle with care so as not to damage the inverter during transportation

• Do not hold only the faceplate (plastic section) but the die-cast section.

## LOCATION

Location of the equipment is important to achieve proper performance and normal operating life.

The 7200M3 units should be installed in areas where the following conditions exist.

•Ambient temperature:

-10 to +40°C ,+14 to 104°F (For enclosed type) ,

-10 to +45ºC ,+14 to 113ºF (For open chassis type)

•Protected from rain or moisture.

•Protected from direct sunlight.

•Protected from corrosive gases or liquids.

•Free form airborne dust or metallic particles.

•Free form vibration.

•Free form magnetic noise.

MOUNTING SPACE

Unit : mm

30mm        30mm

100mm

7200M3

100mm

Fig 1.1 Mounting Space

1.4  WIRING

Connect main circuit and control circuit wiring securely as descrined in the following.

1.4.1  Terminal Cover Mounting/Removing

Please see the 7200M3 manual page 4.

For removing terminal cover, first remove the operator, then press the cover in direction of  1  (on both sides) and, at the same time, lift in direction of  2  . For mounting, reverse the procedure. The figure below shows how to unlock (in direction of  1  ) and lock (in direction of  2  ) the ribbon cable between the digital operator and the inverter.

Please see the 7200M3 manual page 4.

1.4.2 Standard Wiring Diagram

Models with digital operator can be operated from the digital operator (JNEP--13) only by main circuit wiring. When these models are operated by control circuit terminals, control constant change is required. For details, refer to RUN STOP PROCEDURE SELECTION” on page 68. Models with analog operator (JNEP--14) re preset in operation mode from control circuit terminals at the factory prior to shipping.

- Run by digital operator

BRAKING RESISTOR UNIT (OPTION)

B

B1/P

(R)

(S)

(T)

1

COMPENSATION RESISTOR FOR FREQUENCY METER SCALE 
RV30YN20SB 20kΩ

2

CONNECT IF NECESSARY

3

MULT1-FUNCION CONTACT INPUT

4

A

B

C

FM

8

9

13

14

MULTI-FUNCTION OUTPUT

OPEN COLLECTOR 2

IM

FM

STAND SETTING OUTPUT FREQUENCY 0 TO +10V

“AGREED FREQUENCY SIGNAL”

IS SET AT FACTORY

SEQUENCE COMMON (0V)

SHIELDEDTERMINAL

SPEED SETTING POWER SUPPLY+12V 20mA

SPEED REF. 0 - 10V (20kΩ)

4 - 20mA (250Ω)

0V

7200M3

(U)

(V)

(W)

E

MOTOR

5

7

11

6

P

P

0V

FWD RUN/STOP

2kΩ

0 to +10V

4 to 20mA

B2

P

(R)

(S)

(T)

GROUNDING

EXT. FAULT

JOG REF.

EXT.
BASEBLOCK

POWER SUPPLY

Only terminal R,S

For single phase series

MASTER

FREQUENCY REF

12

11

ANALOG MONITOR

10

FREQUENCY METER
(SPEC : DC 3V 1mA)

DEFECTIVE CONTACT OUTPUT 
250V AC 1A OR LESS
30V DC 1A OR LESS

MULTI-FUNCTION OUTPUT OPEN COLLECTOR 1

“ZERO SPEED SIGNAL” IS SET AT FACTORY SETTING 48V 50mA

MULTI-FUNCTION ANALOG OUTPUT

Fig 1.2 Standard Wiring Diagram

(Digital Operator)

Run by analog operator

BRAKING RESISTOR UNIT (OPTION)

(R)

(S)

FWD RUN

STOP

RESET

SEQUENCE COMMON (0V)

SHIELDEDTERMINAL

SPEED SETTING POWER SUPPLY+12V 20mA

SPEED REF. 0 - 10V (20kΩ)

4 - 20mA (250Ω)

0V

6

10

FM

8

9

ANALOG OUTPUT

11

ANALOG OPERATOR

(JNEP- -14)

MULTI-FUNCTION OUTPUT

OPEN COLLECTOR 2

IM

7200M3

(T)

(U)

(V)

(W)

E

MOTOR

1

2

3

12

7

11

13

14

P

0V

FWD RUN/STOP

2kΩ

0 to +10V

B1/P

B2

P

B

(R)

(S)

(T)

GROUNDING

POWER SUPPLY

Only terminal R,S

For single phase series

MULT1-FUNCION CONTACT INPUT

MASTER

FREQUENCY REF

MULTI-FUNCTION OUTPUT OPEN COLLECTOR 1

“ZERO SPEED SIGNAL” IS SET AT FACTORY SETTING 48V 50mA

Fig 1.3 Standard Wiring Diagram (Analog Operator)

Notes:

1.             Indicates shielded leads and               p  twisted-pair shielded leads.

2.External terminal (10) of +12V has maximum output current capacity of 20 mA.

3.Terminal Symbols:      shows main circuit;      shows control circuit.

*Set thermal overload relay between braking resistor and inverter when using braking resistor (type ERF-150WJ) to protect braking resistor from overheating.

Also, use sequencer to break power supply side on thermal overload relay trip contact when using braking resistor.

    - Main Circuit

- Main circuit wiring

Connect wiring as shown in Fig.1.4

BRAKING RESISTOR

(OPTION)

P

B1/P

(R)

(S)

(T)

1

IM

7200M3

(U)

(V)

(W)

E

MOTOR

2

B2

B

(R)

(S)

(T)

GROUNDING

POWER SUPPLY

Only terminal R,S

For single phase series

Fig.1.4 Main Circuit Wiring

- Main circuit terminals

Table 1.1 7200M3 Main Circuit Terminals

| Terminal | Description |
| --- | --- |
| R | Main circuit power input R , S are used for single-phase input specifications. |
| S |  |
| T |  |
| U | Inverter output |
| V |  |
| W |  |
| B1/P | Braking resistor (options) |
| B2 |  |
| E* | Grounding (ground resistance should be 100 ohms or less) |

* Use screw for frame ground.

• Main circuit terminal arrangement

3-Phase series (all models)                 220V single-phase series

| R # R; S; B1/P; B2; U; V; W. | S | T | B1/P | B2 | U | V | W |
| --- | --- | --- | --- | --- | --- | --- | --- |

BLANK

- Molded-case circuit breaker (MCCB) and power supply magnetic contactor.  (MC)

Be sure to connect MCCBs between AC main circuit power supply and 7200M3, input terminals R , S , T, to protect wiring. Recommended MCCBs are listed in Table1.2.

When a ground fault interrupter is used, select one not influenced by high frequency. Setting current should be 200mA or more and operating time, 0.1sec or more to prevent malfunctions.

Table 1.2 Molded-case Circuit Breakers and Magnetic Contactors

•220V Class (3-Phase & Single-Phase Input Series)

| Voltage Class 220V 3-phase 220V Single-phase |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Inverter model JNTABDCB JK--- JNTBBDCB JK--- |  |  |  |  |  |  |  |  |  |  |  |
| R500 | 0001 | 0002 | 0003 | 0005 | 7R50 | 0010 | R500 | 0001 | 0002 | 0003 | 0005 |
| Capacity KVA 1.4 | 2.1 | 2.7 | 4.1 | 6.9 | 10.3 | 13.7 | 1.4 | 2.1 | 2.7 | 4.1 | 6.9 |
| Rated Output 3.2 Current A | 4.8 | 6.5 | 9.6 | 16 | 24 | 32 | 3.2 | 4.8 | 6.5 | 9.6 | 16 |
| MCCB 5A | 10A | 20A | 20A | 30A | 50A | 60A | 10A | 20A | 20A | 40A | 50A |
| TAIAN CN-11 Magnetic Contactors Model | CN-11 | CN-11 | CN-11 | CN-16 | CN-18 | CN-25 | CN-11 | CN-11 | CN-16 | CN-18 | CN-25 |

•440V  Class (3-Phase Input Series)

| Voltage Class | 440V 3-phase |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Inverter model | JNTABDCB AZ--- |  |  |  |  |  |  |
|  | R500 | 0001 | 0002 | 0003 | 0005 | 7R50 | 0010 |
| Capacity KVA | 1.4 | 2.2 | 3.4 | 4.1 | 6.9 | 10.3 | 13.7 |
| Rated Output Current A | 1.6 | 2.6 | 4 | 4.8 | 8 | 12 | 16 |
| MCCB | 5A | 10A | 10A | 10A | 20A | 20A | 30A |
| TAIAN Magnetic Contactors Model | CN-11 | CN-11 | CN-11 | CN-11 | CN-18 | CN-18 | CN-25 |

- Surge  absorber

The surge absorbers should be connected to the coils of control relays , magnetic contactors ,magnetic valves ,or magnetic brake used for the 7200M3 periphery. Otherwise ,large surge voltage occurs at switching and may cause devices to be damaged or to malfunction. Select type from Table 1.3.

Table 1.3 Surge Absorbers

| Coils of Magnetic Contactor and Control Relay |  | Surge Absorber* |  |
| --- | --- | --- | --- |
|  |  | Model DCR2- | Specifications |
| 200V to 230V | Large-size Magnetic Contactors | 50A 22E | 220 VAC 0.5uF 200 ohm |
|  | Control Relay MY-2,-3(OMRON) HH-2, -23(FUJI) MM-2,-4(OMRON) | 10A 25C | - VAC 0.1uF 100 |
| 380 to 460 V Units |  | 50D 100B | 1000 VDC 0.5uF 220 ohm |

*Made by MARCON Electronics.

(5)Wire and terminal screw sizes

Table 1.4 shows wire sizes and types.

Table 1.4 Wire Size

˙220V Class 3-phase Input Series

| Circuit | Model JNTAABD-CB | Inverter Capacity (KVA) | Terminal Symbol | Terminal Screw | Wire Size | Wire Type |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | AWG | mm² |  |
| Main Circuit | R500JK--- | 1.4 | R, S, T, B1/P, B2, U, V, W E | M4 | 1 4 –10 14 -10 | 2 to 5.5 2 to 5.5 | Power cable: 600V vinylsheathed lead or equivalent |
|  | 0001JK--- | 2.1 | R, S, T, B1/P, B2, U, V, W E | M4 | 1 4 –10 14 -10 | 2 to 5.5 2 to 5.5 |  |
|  | 0002JK--- | 2.7 | R, S, T, B1/P, B2, U, V, W E | M4 | 12 -10 14 -10 | 3.5 to 5.5 2 to 5.5 |  |
|  | 0003JK--- | 4.1 | R, S, T, B1/P, B2, U, V, W E | M4 | 12 -10 14 -10 | 3.5 to 5.5 2 to 5.5 |  |
|  | 0005JK--- | 6.9 | R, S, T, B1/P, B2, U, V, W E | M4 | 12 -10 14 -10 | 3.5 to 5.5 2 to 5.5 |  |
|  | 7R50JK--- | 10.3 | R, S, T, B1/P, B2, U, V, W E | M5 | 10 -8 14 -10 | 5.5 to 8 2 to 5.5 |  |
|  | 0010JK--- | 13.7 | R, S, T, B1/P, B2, U, V, W E | M5 | 10 -8 14 -10 | 5.5 to 8 2 to 5.5 |  |
| Control Circuit | Common to All Models |  | 1 ~ 14 , A , B , C | M3.5 | 20 -14 | 0.5 to 2 | Shielded lead or equivalent |

Table 1.4 Wire Size (Cont’d)

### 220  V Class Single-phase Input Series

| Circuit | Model JNTBB DCB | Inverter Capactiy(KVA) | Terminal Symbol | Terminal Screw | Wire Size | Wire Type |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | AWG | mm² |  |
| Main Circuit | R500JK--- | 1.4 | R, S, T, B1/P B2, U, V, W | M4 | 14 –10 | 2 to 5.5 | Power cable: 600V vinylsheathed lead or equivalent |
|  |  |  | E |  | 14 –10 | 2 to 5.5 |  |
|  | 0001JK--- | 2.1 | R, S, T, B1/P B2, U, V, W | M4 | 14 –10 | 2 to 5.5 |  |
|  |  |  | E |  | 14 –10 | 2 to 5.5 |  |
|  | 0002JK--- | 2.7 | R, S, T, B1/P B2, U, V, W | M4 | 14 –10 | 2 to 5.5 |  |
|  |  |  | E |  | 14 –10 | 2 to 5.5 |  |
|  | 0003JK--- | 4.1 | R, S, T, B1/P B2, U, V, W | M4 | 12 -8 | 3.5 to 8 |  |
|  |  |  | E |  | 14 –8 | 2 to 8 |  |
|  | 0005JK--- | 6.9 | R, S, T, B1/P B2, U, V, W | M4 | 10 -8 | 5.5 to 8 |  |
|  |  |  | E |  | 14 –8 | 2 to 8 |  |
| Control Circuit | Common to All Models |  | 1˜ 14, A, B, C | M 3.5 | 20 -14 | 0.5 to 2 | Shielded lead orequivalent |

˙440V Class 3-phase Input Series

| Circuit | Model JNTAB DCB | Inverter Capactiy (KVA) | Terminal Symbol | TerminalScrew | Wire Size | Wire Type |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | AWG | mm² |  |
| Main Circuit | R500AZ--- | 1.4 | R, S, T, B1/P B2, U, V, W | M4 | 14 -10 | 2 to 5.5 | Power cable:600Vvinylsheathed lead or equivalent |
|  |  |  | E |  | 14 -10 | 2 to 5.5 |  |
|  | 0001AZ--- | 2.2 | R, S, T, B1/P B2, U, V, W | M4 | 14 -10 | 2 to 5.5 |  |
|  |  |  | E |  | 14 -10 | 2 to 5.5 |  |
|  | 0002AZ--- | 3.4 | R, S, T, B1/P B2, U, V, W | M4 | 14 -10 | 2 to 5.5 |  |
|  |  |  | E |  | 14 -10 | 2 to 5.5 |  |
|  | 0003AZ--- | 4.1 | R, S, T, B1/P B2, U, V, W | M4 | 14 -10 | 2 to 5.5 |  |
|  |  |  | E |  | 14 -10 | 2 to 5.5 |  |
|  | 0005AZ--- | 6.9 | R, S, T, B1/P B2, U, V, W | M4 | 14 -10 | 2 to 5.5 |  |
|  |  |  | E |  | 14 -10 | 2 to 5.5 |  |
|  | 7R50AZ--- | 10.3 | R, S, T, B1/P B2, U, V, W | M5 | 12 -10 | 3.5 to 5.5 |  |
|  |  |  | E |  | 14 -10 | 2 to 5.5 |  |
|  | 0010AZ--- | 13.7 | R, S, T, B1/P B2, U, V, W | M5 | 12 -10 | 3.5 to 5.5 |  |
|  |  |  | E |  | 14 -10 | 2 to 5.5 |  |
| Control Circuit | Common to All Models |  | 1`˜ 14, A, B, C | M3.5 | 20 -14 | 0 .5 to 2 | Shielded lead or equivalent |

NOTE

Lead size should be determined considering voltage drop of leads.Voltage drop can be obtained by the following equation:select such lead size that voltage drop will be within 2% of normal rated voltage.

Phase-to-phase voltage drop(V)= √3× lead resistance(ohm/km)×wiring distance(m)  ×current(A) ÷ 10 ³

˙Insertion of power supply coordination AC reactor

When the power supply capacity exceeds 600 KVA, connect an AC reactor at the inverter input side for power supply coordination. This reactor is also effective for power factor improvement of the power supply.

˙Wiring length between inverter and motor

If total wiring distance between inverter and motor is excessively long and inverter carrier frequency (main transistor switching frequency) is high, harmonic leakage current from the cable willincrease to affect the inverter unit or peripheral devices. If the wiring distance between inverter and motor is long, reduce the in verter carrier frequency as shown below.  Carrier frequency can be set by constant Pn-40.  For details, refer to “CARRIER FREQUENCY SETTING” on page 89. Carrier frequency is set to 10 KHz at the factory prior to shipping.

| Wiring Distance between Inverter and motor | Up to30 m | Up to50 m | Up to 100 m | 100 m or more |
| --- | --- | --- | --- | --- |
| Allowable Carrier Frequency (Constant Pn40 Set Value) | 15KHz or less(6) | 10KHz or less(4) | 5KHz or less(2) | 2.5KHz or less(1) |

(6)  Wiring

(a)Main circuit input/output

(1)Phase rotation of input terminals R, S, T is available in either direction, clockwise or counterclockwise.

(2)When inverter output terminals U, V, W are connected to motor terminals (U, V, W) respectively, motor rotates counterclockwise, when viewed from opposite drive end, upon forward run command.To reverse the rotation, interchange any two of the motor leads.

(3)Never connect AC main circuit power supply to output terminals U, V, W. Inverter may be damaged.

(4)Insert an L noise filter to the 7200M3 output, but never connect power factor correction capacitor, LC or RC to 7200M3 output.

(5) Be sure to tighten the main circuit terminal screws.

(6) Be sure to separate the main circuit wiring from inverter and peripheral device control lines.Otherwise, it may cause the devices to malfunction.

(b)Grounding

(1)Ground the casing of the 7200M3 using ground terminal E. Ground resistance should be 100ohm or less.

(2)Never ground 7200M3 in common with welding machines, motors, or other large-current electrical equipment,or a ground pole. Run the ground lead in a conduit separate from leads for large-current electrical equipment.

(3)Use the ground leads which comply with A WG standards and make the length as short as possible.

(4)Where several 7200M3 units are used side by side, all the units should be grounded as shown in (a) or (b) of Fig 1.5. Do not from a loop with the groundleads as shown in (c).

(a) GOOD         (b) GOOD        (c) POOR

Fig.1.5 Grounding of Three 7200M3 Unit

1.4.4  Control Circuit

(1)Control circuit wiring

Fig.1.6 shows the relation between the I/O signals (factory pre-set values) and screw terminal numbers. The control signals are connected by screws. The terminal functions shown in the figure indicate standard setting prior to shipping. Since operation mode from the digital operator is set for the model with the digital operator, it is necessary to change the control constants when operation is performed from the control circuit terminals.

For the model with analog operator (JNEP--14) operation mode from the control circuit terminals is the standard setting preset at the factory prior to shipping.

BRAKING RESISTOR UNIT (OPTION)

B

B1/P

(R)

(S)

(T)

1

COMPENSATION RESISTOR FOR FREQUENCY METER SCALE 
RV30YN20SB 20kΩ

2

CONNECT IF NECESSARY

3

MULT1-FUNCION CONTACT INPUT

4

A

B

C

FM

8

9

13

14

MULTI-FUNCTION OUTPUT

OPEN COLLECTOR 2

IM

FM

STAND SETTING OUTPUT FREQUENCY 0 TO +10V

“AGREED FREQUENCY SIGNAL”

IS SET AT FACTORY

SEQUENCE COMMON (0V)

SHIELDEDTERMINAL

SPEED SETTING POWER SUPPLY+12V 20mA

SPEED REF. 0 - 10V (20kΩ)

4 - 20mA (250Ω)

0V

7200M3

(U)

(V)

(W)

E

MOTOR

5

7

11

6

P

P

0V

FWD RUN/STOP

2kΩ

0 to +10V

4 to 20mA

B2

P

(R)

(S)

(T)

GROUNDING

EXT. FAULT

JOG REF.

EXT.
BASEBLOCK

POWER SUPPLY

Only terminal R,S

For single phase series

MASTER

FREQUENCY REF

12

11

ANALOG MONITOR

10

FREQUENCY METER
(SPEC : DC 3V 1mA)

DEFECTIVE CONTACT OUTPUT 
250V AC 1A OR LESS
30V DC 1A OR LESS

MULTI-FUNCTION OUTPUT OPEN COLLECTOR 1

“ZERO SPEED SIGNAL” IS SET AT FACTORY SETTING 48V 50mA

MULTI-FUNCTION ANALOG OUTPUT

Fig 1.6 Standard Wiring Diagram

(2) Control circuit terminals (factory preset)

- CONTROL CIRCUIT

| Classi- fication | Terminal | Signal Name | Function |  |  |  | Signal level |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sequence Input Signal | 1 | Forward operation-stop signal | Forward run at closed, stop at open |  |  |  | Photo-coupler insulation input +24V DC 8mA |  |
|  | 2 | Reverse operation-stop signal | Reverse run at closed, stop at open |  |  |  |  |  |
|  | 3 | Fault reset input | Reset at closed |  |  |  |  |  |
|  | 4 | External fault input | Fault at closed | Multifunction contact input: Two signals available to select. (Note 1) |  |  |  |  |
|  | 5 | Multi-step speed ref. 1 | Effective at “closed” |  |  |  |  |  |
|  | 6 | Sequence control input common terminal | -------------- |  |  |  |  |  |
| Analog Input Signal | 10 | Power supply terminal for speed ref. | Speed ref. power supply |  |  |  | +12V (Allowable current 20mA max.) |  |
|  | 8 | Speed frequency ref. | 0 to +10V/ Max. Output freq. |  |  |  | 0 to +10V (20kΩ) |  |
|  | 9 |  | 4 to 20Ma/ Max. Output freq.. |  |  |  | 4 to 20Ma (250Ω) |  |
|  | 11 | Common terminal for control circuit | 0 v |  |  |  | ----------- |  |
| Sequence Output Signal | 13 | During running (NO) | “L” level at Run |  | Multifunction contact input: Two signals available to select. (Note 2) |  | Open collector output +48V 50Ma or less |  |
|  | 14 | Speed agreed detection | “L” level at set. Frequency = output freq. |  |  |  | Open collector output +48V 50Ma or less |  |
|  | 7 | Open collector output common |  |  |  |  | --------- |  |
|  | A | Fault contact output common (NO, NC) | Fault at closed between terminals A and C Fault at open between terminals B and C |  |  |  | Dry contact Contact capacity: 250VAC 1A or less 30VDC 1A or less |  |
|  | B |  |  |  |  |  |  |  |
|  | C |  |  |  |  |  |  |  |
| Analog Output signal | 21 | Frequency meter output | 0 to 10V/ Max. output frequency. Possible to select current meter output. (Note 3) |  |  | 0 t0 11 V max. 2 mA or less |  |  |
|  | 22 | Common |  |  |  |  |  |  |

NOTE: 1. For details, refer to “MULTIFUNCTION CONTACT INPUT FUNCTION SELECTION’’ on page84.

2. For details, refer to “MULTIFUNCTION PHOTO-COUPLER OUTPUT FUNCTION SELECTION” on page 86.

3. For details, refer to “MULTIFUNCTION ANALOG MONITOR SETTING on page 76.

˙Control circuit terminal arrangement

| A | B | C 1; 2; 3; 4; 5; 6; 7; 8; 9; 10; 11; 12; 13; 14. |
| --- | --- | --- |

(3) Precautions on control circuit wiring

• Separate the control signal line from power lines.  Otherwise, it may cause a malfunction.

• For frequency setting signal (analog), use shielded lead and conduct termination sufficiently.

• Wiring length of the control signal line must be 50 m or less.

• To drive the contact input signal by transistor, use one having ratings of 50V 50m A or more. Circuit leakage current at signal OFF must be 100 A or less.

• To drive an inductive load (relay coil, etc.) by multifunction photo coupler output, be sure to insert a free wheel diode.

48v max.

13,14

Free Wheel Diode

(100v 100mA 0r More)

7

7200M3

1.5 OPERATION

1.5.1 Pre-operation Check

Check the following items after completion of installation and wiring:

(1) No fault in wiring.

Never connect AC main circuit power supply to output terminal (U, V, W)

(2) No short circuit because of wiring contamination (dust, oil, etc.)

(3) Screws and terminals are tightened. Wiring is proper.

Load status is good.

(4) For safe operation, the motor must be able to operate alone by separating it from the coupling of belt, which connects the motor and the machine. Pay close attention when the motor is operated with the machine directly connected.

(5) Wiring is not grounded.

(6) Run command is not input.

When the forward/reverse run command is input in the operation mode (factory setting for the model with blank cover) from the control circuit terminal, the motor is activated automatically after the main circuit power supply is turned on. Turn on the inverter power supply after checking that the run command is not input.

1.5.2 Pre-operation Setting

Since the standard inverter models are provided with the values indicated in Par. 2.8 (see page 58 and beyond), the digital operator (JNEP--13) must be used in order to change the constants from the initial values to the values in accordance with the load specifications.

The following describes the functions and initial constant set values which ere often used for operation.

Output frequency and

accel / decel  time

Frequency setting signal

and output frequency

| The maximum output frequency is set to 60 Hz and accel/decel time to 10 seconds at the factory prior to shipping .To change the values, refer to “ACCEL/DECEL TIME SETTING” on page 71. OUTPUT FREQ. 0.25 10v Frequency setting voltage (v) Accel. Time decel.Time 10 sec 10 sec 60 Hz output Freq. (Hz) Fig. 1.7 Output Frequency and Accel/Decel Time | Fig 1.8 shows the inverter output frequency for control circuit terminal master frequency reference voltage. To change the value, refer to “FREQUENCY COMMAND GAIN/BIAS” on page 78. Fig. 1.8 Frequency Setting Signal and Output Frequency |
| --- | --- |

V / F characteristics

Motor rated current setting

| 220 (V) 0 1.5 3 50 60 14 8 Fig. 1.9 shows the output voltage for inverter output frequency. When its characteristic (max.voltage/frequency) differs from that of the optimum motor, refer to “V/f CHARACTERISTIC SETTING” on page 69. (Hz) *For 440 V class, the value is twice that of 220 V class. Fig. 1.9 V/f Characteristics | Since the inverter is provided with an electronic thermal overload protective function in order to protect the motor from overheating, set the rated current value described on the motor nameplate to constant (Pn-19). TECO standard 4-pole motor current value is set as the initial value .For details, refer to “ELECTRONIG THERMAL OVERLOAD FUNCTION” on page 74. Note: Provide a thermal overload relay or thermal protector for each motor when more than two motors are operated simultaneously. |
| --- | --- |

1.5.3 Test Run Method

The inverter can be operated in the following two ways .The model with digital operator is set to “OPERATION MODE BY DIGITAL OPERATOR” and the model with analog operator (JNEP--14) is set to “OPERATION MODE FROM CONTROL CIRCUIT TERMINAL” prior to shipping.

Run by digital operator

(Standard setting of model

with digital operator )

Run by control circuit terminal input ( Standard Setting of model with analog operator)

| This method is to operate the inverter by using the RUN (run command) key, etc. of the digital operator. Since this operation mode is set at the factory prior to shipping, operation can be performed only by main circuit wiring. For details of the operation method, refer to Section 2 beginning on page 43. JNEP--12 7200M3 POWER IM JNEP--13 | This method is to operate the inverter by frequency setter or operation switch connected to the control circuit terminal. To perform operation by control circuit terminal input of the model with digital operator, change the operation mode to “ OPERATION FROM CONTROL CIRCUIT TERMINAL” (Pn-01=0000). POWER JNEP--14 7200M3 IM |
| --- | --- |

POWER ON

Operation by control circuit

(Standard setting of models with analog operator)

Operation by digital operator

(Standard setting of models

with digital operator ) (Note 2)

| Operation Method Selection | Need not to change the mode since operation mode by digital operator is set at the factory. | ˙Enter the program mode (depress PRG/DRV key) and set Pn-01 data 0000 by using UP, DOWN Or SHIFT key. Then depress DATA key. • Enter the drive mode. (depress PRG/DRV key). • After above operation, command from control circuit terminal can be received. (Note) |
| --- | --- | --- |
| Operation | ˙Select frequency reference value display F000.0 by depressing DSPL key on digital operator. • Depress DATA key after setting frequency value by using , or SHIFT key. • Depress RUN key. | ˙Turn the frequency setter knob to the left to decrease value fully. (Frequency reference=0) • Turn on FWD or REV run signal. • Turn the frequency setter knob slowly to the right to increase value fully. |
| Stopping | ˙Depress RUN key. | ˙Turn the frequency setter knob slowly to the left to decrease value fully. • Turn off FWD or REV run signal. |

Note: 1. Models with analog operator (the standard setting preset at the factory prior to shipping) need not this operation.

2.Refer. to Par.2.2  “DIGITAL OPERATOR OPERATION EXAMPLE”

(Page 49)  for details of digital operator operation.

    - Inverter Status Display LED

With the model with analog operator or free kit operator, LED provided for the inverter is of help to know the inverter status. This LED can be seen by removing the terminal cover or from the right side without removing the cover. Inverter status can be seen by the LED lighting modes. Table 1.6 shows the LED lighting modes and the contents. Check that the inverter is in the normal status at power ON in the test run stage. Free kit operator (JNEP--15) has are LED on the operator cover also, it display the same inverter status as showing in table 1.6.

Table 1.6 LED Display and Contents

| Inverter Status | LED Display DSI (RED.) | Display Contents | Remarks |
| --- | --- | --- | --- |
| Normal |  | Operation ready (during STOP) |  |
|  |  | During normal RUN |  |
| Alarm |  | Power supply voltage reduction, external BB inputting. Etc. in STOP status | Automatic recovery by protective operation release |
| Protective operation |  | Inverter external fault (EF is input). | Can be reset by removing the factor. (Hardware fault if not recovered) |
|  |  | Overload protection such as inverter overload (OL.), fin overheat, etc. |  |
|  |  | Voltage protection such as over voltage (OV) under voltage (UV) |  |
|  |  | Over current protection (OC) |  |
| Inverter fault | ● | Digital hardware memory fault (CPF) | Cannot be reset (replace the inverter) (Note 1) |
|  |  | Hardware fault such as control power supply fault, CPU runaway, etc. | Cannot be reset. (Replace the inverter). |

● : LED light off,       : LED blink,            :LED light

Note 1. By initializing control constants using the digital operator, errors may be released. For details of constant initialization, refer to “DISPLAY OF OPERATOR” on page 67.

1.5.5 Digital Operator Display

When the inverter power supply is turned ON for the first time, the digital operator displays as shown below. If an alarm is displayed, refer to Par 1.7 “FAULT DISPLAY AND TROUBLESHOOTING” on page 26 to remove the factor.

1.   2.     3.

1. Drive mode display (DRV): Lights.

2. Rotating direction display (FWD): Lights

(REV): Extinguished

3. EXT mode display (EXT RUN, CMD):

Extinguished.

4 .During RUN display (RUN):

5. During STOP display (STOP): Lights.

6. 7-segment LED display (5digits):

Output frequency reference set value

F000.0

4.        5.

1.5.6 Check Points at Test Run

The following describes the checkpoints at test run. If any fault occurs, recheck the wiring and load status. For details, refer to Par. 1.7.3 “Corrective Action for Motor Faults” onpage31.

• Motor rotates smoothly.

• Motor rotates in the proper direction.

• Motor does not have any abnormal vibration or beat.

• Acceleration or deceleration goes smoothly.

• Current suitable for load flows.

• Status display LED or digital operator display is proper.

#### CAUTIONS

(1) The motor does not start up if both FWD and REV run signals are turned ON simultaneously. If they are turned ON simultaneously during run, the motor stops according to the stopping method selection of constant (Pn-01) 3 rd digit. (Deceleration to a stop is selected for factory setting.)

(2) When output frequency is reduced to 1.5 Hz (preset value prior to shipping) at deceleration, the DC injection braking operates for 0.5 second (preset value prior to shipping) and metallic noise is generated by the motor. However, this noise is normal. To eliminate this noise, refer to “DC INJECTION BRAKING” on page 80.

(3) If a fault occurs during acceleration or deceleration and the motor coasts to a stop, check the motor stop and then the following items. For details, refer to Par. 1.7 “FAULT DISPLAY AND TROUBLESHOOTING” on page 26.

• Load is not excessively large.

• Accel/decel time is long enough for load.

(4) Resetting must be performed by fault reset input signal (or SHIFT key of the digital operator) or by turning OFF the power supply.

(5) In a sequence where run/stop is performed by the magnetic contactor for main circuit power supply, the repeating time (power ON interval to the inverter) must be one hour or more.

1.6 MAINTENANCE

1.6.1 Periodical Inspection

7200M3 requires very few routine checks .It will function longer if it is kept clean cool and dry, while observing the precautions listed in “Location” (Par.1.3). Check for tightness of electrical connections, discoloration or other signs of overheating. Use Table 1.7 as the inspection guide. Before servicing, turn OFF AC main circuit power and be sure that CHARGE lamp is OFF.

Table 1.7 Periodical Inspections

| Component | Check | Corrective Action |
| --- | --- | --- |
| External Terminals, Unit Mounting Bolts, Connectors, etc. | Loosened screws | Tighten |
|  | Loosened connectors | Tighten |
| Cooling Fins | Build-up of dust or dirt | Blow with dry compressed air of 392 ×10³ to 588×10³ Pa[57 to 85 1bs.. in² (4 to 6 kg. cm²)]pressure.. |
| Printed Circuit Board | Accumulation of conductive dust or oil mist | Clean the board. If dust and oil cannot be removed, replace the inverter unit |
| Cooling Fan | Abnormal noise or vibration. Whether the cumulative operation time exceeds 20,000 hours or not | Replace the inverter unit. |
| Power Elements | Accumulation of dust or dirt |  |
| Smoothing Capacitor | Discoloration or odour | Replace the inverter unit. |

1.6.2 High Voltage Test

Use an insulation resistance tester (500V) to conduct insulation resistance test (high voltage test) on the main control circuit as described below.

(1) Remove the inverter main circuit and control circuit terminal wiring and execute the test only between the main circuit terminals and ground [ground terminal E] as shown in Fig.1.10.

(2) The equipment is normal with the insulation resistance tester indicating 1MΩ   or more.

7200M3

R  S  T  U  V W  B1/P B2        E

Note: Do not conduct high voltage test on the control circuit terminals.

Fig.1.10 High Voltage Test

1.7 FAULT DISPLAY AND TROUBLESHOOTING

If a fault occurs and the inverter functions are lost, check for the causes and provide proper corrective actions, referring to the following checking method.

Contact your TECO representative if any fault other than described below occurs, if the inverter itself malfunctions, if any parts are damaged, or if you have any other problems.

1.7.1 Checking of Causes

The inverter has protective functions to protect it from faults such as overcurrent or overvoltage. If a fault occurs, the protective functions operate to shut off the inverter output and the motor coasts to a stop. At the same time, the fault contact signal is output.

When the protective functions operate in models with analog operator, LED displays a fault show in table 1.6. Also when the digital operator is used, the fault display is provided as shown in table 1.8.

The operation can be restarted by turning ON the fault reset input signal (or RESET key of the digital operator) or turning OFF the power supply and ON again.

Table 1.8 Fault Display and Contents

| Digital Operator fault display | Contents | Possible Cause/ Corrective Actions |
| --- | --- | --- |
| OC (Over-current) | Inverter output current exceeds 200% of rated current. (Momentary action) | The following cause can be considered: inverter output side short-circuits. Excessive short setting of accel/decel time, [constant Pn-09~12] special motor use, motor start during coasting, start of motor with larger capacity than inverter, inverter output side magnetic contactor ON/OFF. Reset after finding the cause. |
| OV (Over-voltage) | Main circuit DC voltage exceeds 410 V or more for 2220 V class. 820 V or more for 440 V class because of excessive regenerative energy from motor. (Exceeds over voltage protection level.) | Decel. time setting is not sufficient. [Constant Pn-10, 12] or minus load (cranes, etc.) is decreasing. Increase decel. time or connect a braking resistor (option). |
| UV (Under-voltage) | Under voltage status is entered. [Main control DC voltage becomes approx. 210 V or less (220 V class 3-phase).170 V or less (220 V class single-phase) or 420 V or less (440 V class 3-phase)]. | Input power supply voltage is reduced, phases are opened or momentary power loss occurs, etc. Check the power supply voltage, or check that main circuit power supply wiring is connected properly or terminal screws are tightened well. |
| OH (Cooling Fin Overheat) | Temperature rise caused by inverter overload operation, or intake air temperature rise. Cooling fan r/min is decreased | Load is too large, V/f characteristic are not proper, setting time is too short or intake air temperature exceeds 113°F (45°C), etc. Correct load size, V/f set value [constant Pn-02~Pn-08] or intake air temperature. Check the cooling fan. |

Table 1.8 Fault Display and Contents (Cont’d)

| Digital Operator fault display | Contents | Possible Cause/ Corrective Actions |
| --- | --- | --- |
| OL1 (Motor Overload) | Motor overload protection operates because of electronic thermal overload. | Correct load size, operation pattern or V/f set value [constant Pn-02~08]. Set the rated current value described in the motor nameplate to constant Pn-19. |
| OL2 (Inverter Overload) | Inverter overload protection operates because of electronic thermal overload. | Correct load size, operation pattern or V/f set value [constant Pn-02~08]. Recheck the inverter capacity. |
| OL3 (Overtorque Detection) | Motor current exceeding set value is applied because of machine fault or overload. | Check the machine using status and remove the cause. Or increase the set value up to the machine allowable value [constant Pn-38]. |
| EF4.5 (Note 2) (External Fault) | Inverter accepts external fault input from external circuit. | Check the external circuitry (sequence). |
| CPF (Note 3) (Control Function Fault) | Inverter control functions are broken down | Turn OFF the power supply once and then turns it ON again. Or initialize the control constant by using the digital operator. If the fault still exists, replace the inverter. |
| Digital display is extinguished. | ˙Main circuit fuse is blown. (For 440V class only) • Control power supply fault • Hardware fault | Replace the inverter. |

Note: 1. For OL3 ( overtorque detection) fault display or alarm display can be selected according to the constant (Pn-37) setting. For details, refer to “OVERTORQUE DETECTION FUNCTION” on page 99.

2. EF4 shows external fault input from multifunction contact input terminal 4,and EF5 from terminal 5.

3. For details of CPF (control function faults) refer to Table 1.9. “Details of CPF Display.

Table 1.9 Details of CPF Display

| Digital Operator fault display | Contents | Possible Cause/ Corrective Actions |
| --- | --- | --- |
| CPF-00 | Digital Operator Communication error 1 | Turn OFF the power supply once and turn it ON again. If the fault still exists, replace the inverter. |
| CPF-01 | Digital Operator Communication error 2 |  |
| CPF-04 | E²PROM fault | Record all data, and then make initialization. Turn OFF the power supply once and turn it ON again. If the fault still exists, replace the inverter. For initialization of constants, refer to Par. 2.5.1 “Constant Initialization” on page51. |
| CPF-05 | AD converter fault in CPU |  |

1.7.2 Alarm Display and Contents

Alarms, among inverter protective functions, do not operate fault contact output and returns to the former operation status automatically when the factor is removed.

The following shows the types and contents.

Table 1.10 Alarm Display and Contents

| Digital Operator fault display | Contents | Possible Cause/ Corrective Actions |
| --- | --- | --- |
| EF (Simultaneous Input of FWD and REV commands) EF blinks. | Both FWD and REV commands are “closed” for 500 ms or larger. Inverter stops according to constants Pn-01. | Check the sequence circuit. |
| BB (External Baseblock) bb blinks. | External baseblock signal is accepted. Inverter stops output. (Operation restarts by releasing the external baseblock signal.) For the external baseblock signal, refer to “MULTIFUNCTION CONTACT INPUT FUNCTION SELECTION” on page 84. | Check the sequence circuit |
| UV (Main Circuit Under-voltage) Uv blinks. | Main circuit DC voltage is reduced less than detection level when inverter is not outputting. | Check the power supply voltage, main circuit power supply wiring connection or terminal screw tightening. |
| OL3 (Overtorque Detection) (Note 1) oL3 blinks | Motor current exceeding the set value flows due to machine fault or overload. Inverter continues operation. | Check the machine using status and remove the cause of the fault. Or increase the set value [constant Pn-38] up to the machine allowable value. |
| OV (Over Voltage) ov blinks | Main circuit DC voltage is more than overvoltage detection level. When inverter is not outputting. | Check the power supply voltage |
| OH (Cooling fin Over Heat) oH blinks | Intake air temperature rises when inverter is not outputting. | Check the intake air temperature. |

Note: 1. For OL3 (overtorque detection) fault display or alarm display can be selected according to the constant (Pn-37) setting .For details, refer “OVERTORQUE DETECTION FUNCTION” on page 88.

1.7.3 Corrective Action for Motor Faults

Table 1.11 shows the check points and corrective actions of motor faults.

Table 1.11 Motor Faults and Corrective Actions

| Fault | Check point | Corrective Action |
| --- | --- | --- |
| Motor does not rotate. | Power supply voltage is applied to power supply terminals R, S, T. (Check that charge lamp is ON.) | • Turn ON the power supply. • Turn OFF the power supply and then ON again. • Check power supply voltage. • Check that terminal screws are tight. |
|  | Voltage is output to output terminals U, V, W (Use rectifier type voltmeter.) | • Turn OFF the power supply and then ON again. |
|  | Load is excessively large. (Motor is locked.) | Reduce the load. (Release the lock.) |
|  | Fault is displayed. | Check according to Par. 1.7.1. |
|  | FWD or REV run command is entered. | Correct the wiring. |
|  | Frequency setting voltage is entered. | ˙Correct the wiring. ˙Check frequency setting Voltage. |
|  | Operation (method selection) mode setting is proper. | Check the operation method Selection mode [constant Pn-01] by using the digital operator. |
| Motor rotating direction is reversed. | Wiring of output terminals U, V, W is correct. | Match them to the phase order of motor U, V, W. |
|  | Wiring of FWD and REV run signals is correct. | Correct the wiring. |

| Fault | Check Point | Corrective Action |
| --- | --- | --- |
| Motor rotates but variable speed is not available. | .Wiring of frequency setting circuit is correct | Correct the wiring. |
|  | Operation (method selection) mode setting is correct. | Check operation method selection mode [constant Pn-01] by digital operator. |
|  | Load is not excessively large. | Reduce the load. |
| Motor r/min is too high (low). | Motor ratings (number of poles, voltage) are proper. | Check the specifications and nameplate. |
|  | Accel/decel ratio by speed changer (gears, etc.) is correct. | Check speed changer (gears etc.) |
|  | Maximum frequency set value is correct. | Check the max. Frequency set value [constant Pn-02] |
|  | Voltage between motor terminals is not excessively reduced. (Use rectifier type Volt-meter) | Check V/f characteristic set value [Constant Pn-02~08] |
| Motor r/min is not stable during operation (Note) | Load is not excessively large. | Reduce the load. |
|  | Load variation is not excessively large. | ˙Reduce the load variation. ˙Increase the inverter or motor capacity. |
|  | 3-phase or single-phase power supply is used. | Connect an Ac reactor to the power supply if single-phase power supply is used. |

Note: Because of motor and load (geared machine) characteristics, motor r/min becomes unstable or motor current ripples.  To correct these problems, changing the inverter control constants may be effective. Refer to “FUNCTIONS FOR REDUCTION OF MACHING VIBRATION OR SHOCK” on page 99 for details of control constants to be changed.

1.8 SPECIFICATIONS

1.8.1 Specifications

| Voltage Class |  | 220 3-phase |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ## Inverter Model |  | JNTABDCB JK--- |  |  |  |  |  |  |
|  |  | R500 | 0001 | 0002 | 0003 | 0005 | 7R50 | 0010 |
| Max. Applicable Motor Output HP (KW) *1 |  | 0.5(0.4) | 1(0.75) | 2(1.5) | 3(2.2) | 5(3.7) | 7.5(5.5) | 10(7.5) |
| Output characteristics | Inverter Capacity KVA | 1.4 | 2.1 | 2.7 | 4.1 | 6.9 | 10.3 | 13.7 |
|  | Rated Output current A | 3.2 | 4.8 | 6.5 | 9.6 | 16 | 24 | 32 |
|  | Max. Output Voltage V | 3-phase 200 to 230V , 50/60 Hz (proportional to input voltage) |  |  |  |  |  |  |
|  | Max. Output Frequency | 400 Hz (available with constant setting) |  |  |  |  |  |  |
| Power Supply | Rated Input Voltage and Freq. | 3-phase 200 to 230V , 50/60 Hz |  |  |  |  |  |  |
|  | Allowable Volt. Fluctuation | ± 10 ％ |  |  |  |  |  |  |
|  | Allowable Freq. Fluctuation | ± 5 ％ |  |  |  |  |  |  |
| Control Characteristics | Control Method | Sine wave PWM |  |  |  |  |  |  |
|  | Freq. Control Range | 0.1 to 400 Hz |  |  |  |  |  |  |
|  | Frequency Accuracy | Digital command: 0.01%, Analog command : 0.1% |  |  |  |  |  |  |
|  | Freq. Setting Resolution | Digital : 0.1 Hz , Analog : 0.06/60Hz |  |  |  |  |  |  |
|  | Output freq. Resolution | 0.1 Hz |  |  |  |  |  |  |
|  | Overload Capacity | 150% rated output current for one minute |  |  |  |  |  |  |
|  | Freq. Setting Signal | 0 to 10v (20kΩ), 4 to 20 mA (250Ω) |  |  |  |  |  |  |
|  | Accel/Decel. Time | 0.1 to 600 sec (accel/decel time setting independently) |  |  |  |  |  |  |
|  | Braking Torque | Approx. 20%(up to 150% possible with optional braking resistor) |  |  |  |  |  |  |
|  | V/F Characteristic | Possible to set any program of v/f pattern |  |  |  |  |  |  |
|  | Stall prevention level | Possible to set operating current |  |  |  |  |  |  |
| Protection Function | Instantaneous OC | Motor coasts to stop at approx. 200% rated current |  |  |  |  |  |  |
|  | Overload | Motor coasts to stop for 1 minute at approx. 150% rated output current |  |  |  |  |  |  |
|  | Motor overload | Electronic thermal overload relay |  |  |  |  |  |  |
|  | Overvoltage | Motor coasts to stop if main circuit voltage exceeds 410v |  |  |  |  |  |  |
|  | Undervoltage | Stop when main circuit DC voltage is approx. 210v or less |  |  |  |  |  |  |
|  | Momentary Power loss | 15ms or longer *2 |  |  |  |  |  |  |
|  | Cooling Fin Overheat | Protected by thermoswitch (only for forced cooling method) |  |  |  |  |  |  |
|  | Power Charge Indication | Charge lamp stays on until main circuit DC voltage drops below 50v |  |  |  |  |  |  |

*1. TECO standard 4-pole motor is used for max. applicable motor output

*2. To select “automatic restart after momentary power loss “ set the 1st digit of constant (Pn-46) to “1”

Automatic restart is available within approx. 1 second for models of 1HP or less or within approx. 2 seconds for models of 2 HP or more.

1.8.1 Specifications (continue)

| Voltage Class |  | 220 Single-phase |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| ## Inverter Model |  | JNTBBDCB JK--- |  |  |  |  |
|  |  | R500 | 0001 | 0002 | 0003 | 0005 |
| Max. Applicable Motor Output HP (KW) *1 |  | 0.5(0.4) | 1(0.75) | 2(1.5) | 3(2.2) | 5(3.7) |
| Output characteristics | Inverter Capacity KVA | 1.4 | 2.1 | 2.7 | 4.1 | 6.9 |
|  | Rated Output current A | 3.2 | 4.8 | 6.5 | 9.6 | 16 |
|  | Max. Output Voltage V | 3-phase 200 to 240V , 50/60 Hz (proportional to input voltage) |  |  |  |  |
|  | Max. Output Frequency | 400 Hz (available with constant setting) |  |  |  |  |
| Power Supply | Rated Input Voltage and Freq. | Single-phase 200 to 240V , 50/60 Hz |  |  |  |  |
|  | Allowable Volt. Fluctuation | ± 10 ％ |  |  |  |  |
|  | Allowable Freq. Fluctuation | ± 5 ％ |  |  |  |  |
| Control Characteristics | Control Method | Sine wave PWM |  |  |  |  |
|  | Freq. Control Range | 0.1 to 400 Hz |  |  |  |  |
|  | Frequency Accuracy | Digital command: 0.01% , Analog command : 0.1% |  |  |  |  |
|  | Freq. Setting Resolution | Digital : 0.1 Hz , Analog : 0.06/60Hz |  |  |  |  |
|  | Output freq. Resolution | 0.1 Hz |  |  |  |  |
|  | Overload Capacity | 150% rated output current for one minute |  |  |  |  |
|  | Freq. Setting Signal | 0 to 10v (20kΩ), 4 to 20 mA (250Ω) |  |  |  |  |
|  | Accel/Decel. Time | 0.1 to 600 sec (accel/decel time setting independently) |  |  |  |  |
|  | Braking Torque | Approx. 20%(up to 150% possible with optional braking resistor) |  |  |  |  |
|  | V/F Characteristic | Possible to set any program of v/f pattern |  |  |  |  |
|  | Stall prevention level | Possible to set operating current |  |  |  |  |
| Protection Function | Instantaneous OC | Motor coasts to stop at approx. 200% rated current |  |  |  |  |
|  | Overload | Motor coasts to stop for 1 minute at approx. 150% rated output current |  |  |  |  |
|  | Motor overload | Electronic thermal overload relay |  |  |  |  |
|  | Overvoltage | Motor coasts to stop if main circuit voltage exceeds 410v |  |  |  |  |
|  | Undervoltage | Stop when main circuit DC voltage is approx. 210v or less |  |  |  |  |
|  | Momentary Power loss | 15ms or longer *2 |  |  |  |  |
|  | Cooling Fin Overheat | Protected by thermoswitch (only for forced cooling method) |  |  |  |  |
|  | Power Charge Indication | Charge lamp stays on until main circuit DC voltage drops below 50v |  |  |  |  |

1.8.1 Specifications (continue)

| Voltage Class |  | 220 3-phase |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ## Inverter Model |  | JNTABDCB JK--- |  |  |  |  |  |  |
|  |  | R500 | 0001 | 0002 | 0003 | 0005 | 7R50 | 0010 |
| Max. Applicable Motor Output HP (KW) *1 |  | 0.5(0.4) | 1(0.75) | 2(1.5) | 3(2.2) | 5(3.7) | 7.5(5.5) | 10(7.5) |
| Environmental characteristics | Mass (Kg) | ---- | 2.5 | 2.5 | 5.0 | 5.0 | 9.5 | 9.5 |
|  | Cooling Method | Self-cooling |  |  | Forced cooling |  |  |  |
|  | Protective Configuration | NEMA 1 (open chassis type also available) |  |  |  |  |  |  |
|  | Location | Indoor (protected from corrosive gases and dust) |  |  |  |  |  |  |

1.8.1 Specifications (continue)

| Voltage Class |  | 220 Single-phase |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ## Inverter Model |  | JNTBBDCB JK--- |  |  |  |  |  |
|  |  | R500 | 0001 | 0002 | 0003 |  | 0005 |
| Max. Applicable Motor Output HP (KW) *1 |  | 0.5(0.4) | 1(0.75) | 2(1.5) | 3(2.2) |  | 5(3.7) |
| Output characteristics | Inverter Capacity KVA | 1.4 | 2.1 | 2.7 | 4.1 |  | 6.9 |
|  | Rated Output current A | 3.2 | 4.8 | 6.5 | 9.6 |  | 16 |
|  | Max. Output Voltage V | 3-phase 200 to 240V , 50/60 Hz (proportional to input voltage) |  |  |  |  |  |
|  | Max. Output Frequency | 400 Hz (available with constant setting) |  |  |  |  |  |
| Mass (Kg) |  | ----- | 4.6 | 4.6 | 6.7 | 7.4 |  |
| Cooling Method |  | Self-cooling |  | Self-cooling Forced cooling |  |  |  |
| Protective Configuration |  | NEMA 1 (open chassis type also available) |  |  |  |  |  |
| Location |  | Indoor(protected from corrosive gases and dust) |  |  |  |  |  |

1.8.1 Specifications (continue)

| Voltage Class |  | 440 3-phase |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ## Inverter Model |  | JNTABDCB AZ--- |  |  |  |  |  |  |
|  |  | R500 | 0001 | 0002 | 0003 | 0005 | 7R50 | 0010 |
| Max. Applicable Motor Output HP (KW) *1 |  | 0.5(0.4) | 1(0.75) | 2(1.5) | 3(2.2) | 5(3.7) | 7.5(5.5) | 10(7.5) |
| Output characteristics | Inverter Capacity KVA | 1.4 | 2.1 | 2.7 | 4.1 | 6.9 | 10.3 | 13.7 |
|  | Rated Output current A | 1.6 | 2.6 | 4 | 4.8 | 8 | 12 | 16 |
|  | Max. Output Voltage V | 3-phase 380 to 460V , 50/60 Hz (proportional to input voltage) |  |  |  |  |  |  |
|  | Max. Output Frequency | 400 Hz (available with constant setting) |  |  |  |  |  |  |
| Power Supply | Rated Input Voltage and Freq. | 3-phase 380 to 460V , 50/60 Hz |  |  |  |  |  |  |
|  | Allowable Volt. Fluctuation | ± 10 ％ |  |  |  |  |  |  |
|  | Allowable Freq. Fluctuation | ± 5 ％ |  |  |  |  |  |  |
| Control Characteristics | Control Method | Sine wave PWM |  |  |  |  |  |  |
|  | Freq. Control Range | 0.1 to 400 Hz |  |  |  |  |  |  |
|  | Frequency Accuracy | Digital command: 0.01% , Analog command : 0.1% |  |  |  |  |  |  |
|  | Freq. Setting Resolution | Digital : 0.1 Hz , Analog : 0.06/60Hz |  |  |  |  |  |  |
|  | Output freq. Resolution | 0.1 Hz |  |  |  |  |  |  |
|  | Overload Capacity | 150% rated output current for one minute |  |  |  |  |  |  |
|  | Freq. Setting Signal | 0 to 10v (20kΩ), 4 to 20 mA (250Ω) |  |  |  |  |  |  |
|  | Accel/Decel. Time | 0.1 to 600 sec (accel/decel time setting independently) |  |  |  |  |  |  |
|  | Braking Torque | Approx. 20%(up to 150% possible with optional braking resistor) |  |  |  |  |  |  |
|  | V/F Characteristic | Possible to set any program of v/f pattern |  |  |  |  |  |  |
|  | Stall prevention level | Possible to set operating current |  |  |  |  |  |  |
| Protection Function | Instantaneous OC | Motor coasts to stop at approx. 200% rated current |  |  |  |  |  |  |
|  | Overload | Motor coasts to stop for 1 minute at approx. 150% rated output current |  |  |  |  |  |  |
|  | Motor overload | Electronic thermal overload relay |  |  |  |  |  |  |
|  | Overvoltage | Motor coasts to stop if main circuit voltage exceeds 820v |  |  |  |  |  |  |
|  | Undervoltage | Stop when main circuit DC voltage is approx. 420v or less |  |  |  |  |  |  |
|  | Momentary Power loss | 15ms or longer *2 |  |  |  |  |  |  |
|  | Cooling Fin Overheat | Protected by thermoswitch (only for forced cooling method) |  |  |  |  |  |  |
|  | Power Charge Indication | Charge lamp stays on until main circuit DC voltage drops below 50v |  |  |  |  |  |  |

*1. TECO standard 4-pole motor is used for max. applicable motor output

*2. To select “automatic restart after momentary power loss “ set the 1st digit of constant (Pn-46) to “1”

Automatic restart is available within approx. 1 second for models of 1HP or less or within approx. 2 seconds for models of 2 HP or more.

1.8.1 Specifications (continue)

| Voltage Class |  | 440v 3-phase |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ## Inverter Model |  | JNTABDCB AZ--- |  |  |  |  |  |  |
|  |  | R500 | 0001 | 0002 | 0003 | 0005 | 7R50 | 0010 |
| Max. Applicable Motor Output HP (KW) *1 |  | 0.5(0.4) | 1(0.75) | 2(1.5) | 3(2.2) | 5(3.7) | 7.5(5.5) | 10(7.5) |
| Environmental characteristics | Mass (Kg) | ---- | 4.5 | 4.6 | 6.4 | 6.7 | 9.5 | 9.5 |
|  | Cooling Method | Self-cooling |  |  | Forced cooling |  |  |  |
|  | Protective Configuration | NEMA 1 (open chassis type also available) |  |  |  |  |  |  |
|  | Location | Indoor (protected from corrosive gases and dust) |  |  |  |  |  |  |

1.8.2 Dimensions

- Digital Operator Type

7200M3

H1

H

W1

D

W

(B) Analog Operator Type

7200M3

H1

H

W1

D

W

Unit : mm

| Operator | Contents | Dimension (mm) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | W | H | D | W1 | H1 | d |
| Digital | 220V 3Ø 0.5~2 HP | 140 | 150 | 150 | 130 | 140 | M4 |
|  | 220V 1Ø 0.5~2 HP 3Ø 3~5 HP 440V 3Ø 0.5~2 HP | 140 | 250 | 171 | 130 | 240 | M4 |
|  | 220V 1Ø 3~5 HP 440V 3Ø 3~5 HP | 205 | 305 | 165 | 180 | 285 | M6 |
|  | 220V 3Ø 7.5~10 HP 440V 3Ø 7.5~10 HP | 205 | 354 | 200 | 180 | 335 | M6 |
| Analog | 220V 3Ø 0.5~2 HP | 140 | 150 | 170 | 130 | 140 | M4 |
|  | 220V 1Ø 0.5~2 HP 3Ø 3~5 HP 440V 3Ø 0.5~2 HP | 140 | 250 | 191 | 130 | 240 | M4 |
|  | 220V 1Ø 3~5 HP 440V 3Ø 3~5 HP | 205 | 305 | 185 | 180 | 285 | M6 |
|  | 220V 3Ø 7.5~10 HP 440V 3Ø 7.5~10 HP | 205 | 354 | 220 | 180 | 335 | M6 |

1.9 OPTIONS AND PERIPHERAL UNITS

| Name | Model (Code No.) | Function | Installing position | Ref. No (3H358 ) |
| --- | --- | --- | --- | --- |
| Extension Cable for Digital Operator | 1m 3H300C0820006 3m 3H300C0800005 | This extension cable is used when the digital operator is used after removing from the inverter front cover. The cable is available in 1-m and 3-m lengths. | On the front cover | D0180005 |
| Frequency Meter | 3M901D3760000 | 60Hz/120Hz. | Separately installed | — |
| R .P. M. Meter | 3M901D4250005 | 0~1800RPM | Separately installed | — |
| Digital Operator | JNEP--13 | The 7200M3 operator has two types of models: with digital operator and with analog operators. Models with digital operators can be operated from the digital operator only by main circuit wiring. | On the inverter front cover | — |
| Free kit Operator | JNEP--15 | Models with free kit operator are operated by control circuit terminals. There is only a LED on the operator, can display the inverter status | On the inverter front cover | — |
| Analog Operator Unit | JNEP--16 | An exclusive control panel for remotely setting frequency and for turning the unit ON/OFF using analog commands (distance up too50m). | Separately installed | — |
| Braking Resistor | ERF-150W (3H333C-001 ) | Shortens the motor deceleration time by causing the regenerative energy to be consumed through the resistor. Available at 100% deceleration torque at 3% ED for resistor unit only. | Separately installed | — |
| Frequency Setting potentiometer | 3H300D1260002 | Including 2kΩ potentiometer, knob and scale plate. | On the inverter front cover | — |

2. DESCRIPTION OF DIGITAL OPERATING SECTIONS

Mode Display LED

Drive Mode Display

Red lamp lights in DRIVE mode and goes out in PRGM mode.

REMOTE Mode

Red lamp lights when controlled by control terminal commands.

SEO: When RUN/STOP signal is selected from terminals.

REF: When frequency ref. Is selected from terminals.

Display

Run Command Key

STOP command is input. (Motor stops in either mode.)*

Red lamp lights by depressing STOP. *

Selects FWD or REV rum.

Effective only in DRIVE mode.

Rotation Direction Display

Red lamp lights in DRIVE mode and goes out in PRGM mode.

Display set, value of each function or monitoring values such as frequency and output current. (5 digits)

Depressing this key changes mode. (DRIVE or PRGM)

Mode Selection Key

Depressing this key changes the Display.

See page 4 for explanation.

Display Selection Key

Depressing this key changes the Display.

See next page for explanation.

Read/Write Key

Changes numeral such as set values and constant signals.

︿ : Increment key

﹀ : Decrement key

Numeral Change Key

Digit Selection Key

Run Command Key to operate by digital operator.

Effective only in drive mode.

While depressing this key, jog speed is selected.

Effective only in DRIVE mode.

Selects numerical digits. Selected digit blinks.

This key resets operation at faults.

* RUN or STOP lamp changes in accordance with the following operations.

INVERTER

OUTPUT

FREQUENCY

RUN

STOP

STOP

FREQUENCY

SETTING

| RUN Lamp | ● |  |  | ● |
| --- | --- | --- | --- | --- |
| STOP Lamp |  | ● |  |  |

●

: Light            : Blink         : Off

2.1 FUNCTION/CONSTANT SETTING

2.1.1 DRV (Drive) Mode and PRG (Program) Mode

Selection of DRV mode or PRG mode can be performed by using the      key when the inverter is stopped. When function selection or a change of set value is required, switch to the PRG mode.

DRV    mode: • Operation is enabled.

RUNUNRUN

STOPOP

JOG

FWD

REV

• An operation can be performed by       ,      ,      or

keys.

• Frequency reference value can be changed during running.

PRG     mode: • Program (function selection, constant setting) can be changed.

• Operation is not enabled.

Display Contents of DRV Mode and PRG Mode

(1) Display contents of the digital operator differ according to selected mode (PRG/DRV).

(2) The constant group to be displayed is changed each time display selection key  DSPL  is depressed.

(3) If a fault occurs, the contents are displayed. Additionally, since the contents of the latest fault are stored, maintenance, inspection or troubleshooting can be performed quickly by checking the contents by digital operator.

POWER ON

DRIV MODE

MODE SWITCHABLE ONLY AT STOPPING

DRIVE

PRGM

PRGM MODE

DRIVE MODE

Pn-

Frequency reference value display setting

Display/setting

Output frequency monitor display

If a fault occurs, the contents are displayed.

Output current

monitor display

Fault reset

RESET

Pn-      display

＊

* Refer to Par. 2.6 ”FUNCTION / CONSTANT LIST “.

2.1.2 Constant Reading and Setting

The 7200M3 has various functions for the optimum operation. The A group functions are those basic to drive motors. The B group are for basic applications. The C group are more advanced application functions. Use it with the set values according to the load conditions or operation conditions of the matching machine. Control constants are read or set by the digital operator. Set constant (Pn-00) as follows:

| ##### Setting Value |  | Description | Note |
| --- | --- | --- | --- |
| ##### Pn-00= | 0 | A group function (Pn-01~19) can not be set | Lock mode |
|  | 1 | A group function (Pn-00~19) can be set/read | Factory Setting |
|  | 2 | A, B group function (Pn-00~29) can be set/read | — |
|  | 3 | A, B, C group function (Pn-00~59) can be set/read | — |

(Typical setting )

*The following shows an example where acceleration time (Pn-09) is changed from 10 seconds to 5 seconds.

*Other constant can be changed in the same operation.

Depress           Key.

Change the value with

Or       Key.

Depress         Key.

Change the value with

,       Or       Key.

Depress         Key and

Check that “End ” is displayed.

(“End” is displayed for 1 second.)

The data are displayed again .

Depress         Key.

DRIVE

PRGM

RESET

DATA

STR

DATA

STR

DSPL

To display constant Pn-

Enter the program mode.

Pn-01

Select constant Pn-

to be set or changed

Pn-09

Constant set value is

displayed

010.0

Constant is set or

changed

005.0

Set value is written in.

End

005.0

Constant Pn- is displayed

Pn- 09

2.1.3 Precautions on Constant Setting

- Perform constant setting securely.

Improper setting may cause functions not to operate or protective function to operate.

(2) Record the constants of which setting has been changed.

Recording the final setting of constants is effective for maintenance or early troubleshooting. Refer to the Par. 2.6 “FUNCTION/ CONSTANT LIST” which has a column for entering setting of constants on page 58.

(3) Change control constants in increments

Do not change the motor control constant setting such as V/f maximum output frequency, etc. rapidly. Change it in increments , checking the motor current or load machine status. Changing setting very rapidly may affect the inverter or machine.

(4) In the following cases are setting error, the set value blinks for 3 seconds and the data before changing are returned.

(a) When a value exceeding the setting range is set.

(b) If the following condition is not satisfied in the multifunction input selection constant setting:

Multifunction input selection 1 (Pn-32)<Multifunction input selection 2(Pn-33).

(c) If the following conditions are not satisfied in the V/f constant setting:

Pn-02>=Pn-04>=Pn-05>=Pn-07

For details, refer to “V/f CHARACTERISTIC SETTING ”on page 69.

(d) If the following condition is not satisfied in the frequency reference constant setting:

Pn-13~17<=Pn-02×Pn-24

For details, refer to “V/f CHARACTERISTIC SETTING” on page 69 and “OUTPUT FREQUENCY LIMIT” on page 79.

(e) If the following condition is not satisfied in the frequency reference upper/lower limit value setting:

Pn-25<=Pn-24

2.2 DIGITAL OPERATOR OPERATION EXAMPLE

The following shows an example of digital operator operation.

Operation Pattern

FWD

RUN 60Hz

INPUT VOLT VOLTAGE SETTING

POWER ON

FWD JOG SELECTION

FREQ. SET

CHANGE

REV RUN

t

FWD

RUN 1.5Hz

STOP

POWER ON

RUN

RUN

REV

RUN 60Hz

- Typical Operation

| Description | Key Operation | Digital Operator Display | Remarks |
| --- | --- | --- | --- |
| DSPL . RESET DATA STR DRIVE PRGM DATA STR . . Turn on power supply Set input voltage Frequency reference value is displayed. Cont’d (ex: 220V) Pn-01 - Select PRGM mode. - Select control constant (Pn- ) - Display Pn-03 data. - Set 220V as input voltage. | Depress three times. |  | LED DRIVE OFF Displayed for 0.5 second. Confirm the display. |

| Description Cont’d | Key Operation | Digital Operator Display | Remarks |
| --- | --- | --- | --- |
| RUN RUN Change Frequency Reference value 60Hz Select DRIVE mode. FWD JOG - Select output Frequency monitor display. - Select rotating direction. (FWD is default at power ON.) - Jog operation. Frequency reference value display is selected. 15Hz Frequency setting - Change reference value. - Set value is written in. - Select output frequency monitor display. FWD run - Running operation. Select frequency reference value display. - Change reference value. - Set value is written in. Select output frequency monitor value. REV run Switch to reverse run. Stop - Decelerate to a stop. | DRIVE PRGM DSPL JOG DSPL RESET DATA STR DATA STR DSPL DSPL RESET DSPL FWD REV RUN STOP Depress Six times. | . . . . . . . . . . . . . . Blinks while decelerating | LED DRIVE lights. LED FWD lights. Stops blinking for two seconds. LED lights. Stops blinking for two seconds. LED REV lights. STOP LED lights. |

2.3 CONSTANT INITIALIZATION AND LOCK PROTECTION

2.3.1 Constant Initialization(Operation to return to factory setting)

- Write in 8 to constant (Pn-00)

| Description | Key Operation | Digital Operator Display | Remarks |
| --- | --- | --- | --- |
| Turn on power supply Frequency reference value is displayed. - Select PRGM mode. - Select constant (Pn-00 ) - Display Pn-00 data. Set Value Change the set value. - Write in the set value. (“End is displayed) The data are displayed | DRIVE PRGM RESET DATA STR DATA STR | . Pn-01 Pn-00 01 08 01 | LED DRIVE OFF (Note 1) Displayed for 0.5 second. Confirm the display. (Note 2) |

Note : 1. Differs according to the setting data before changing

2.The display returns to 01 after write-in. This indicateds that initialization is executed at writing in the data.

2.3.2 Constant lock Protection (Only constant reading possible)

˙The following shows an example where 0 is written in to constant  (Pn-00)[password(Pn-00) setting/reading and the first functions (constant Pn-01 to 19) reading enabled].

| Description | Key Operation | Digital Operator Display | Remarks |
| --- | --- | --- | --- |
| Turn on power supply Frequency reference value is displayed. - Select PRGM mode. - Select constant (Pn-00 ) - Display Pn-00 data. Set Value Change the set value. - Write in the set value. (“End is displayed) The data are displayed | DRIVE PRGM RESET DATA STR DATA STR | . Pn-01 Pn-00 01 00 00 | LED DRIVE OFF (Note) Displayed for 0.5 second. Confirm the display. |

Note: Differs according to the setting data before changing.

For details , refer to “DISPLAY OF OPERATOR” on page 67.

2.4 CORRECTIVE FUNCTION

2.4.1 Output Frequency Bias (Pn-23) and Gain (Pn-22)

Any desired value of output frequency for frequency set value (0 to 10V or 4 to 20mA) can be set.

| Description | Key Operation | Digital Operator Display | Remarks |
| --- | --- | --- | --- |
| - Frequency reference value is displayed. - Select PRGM mode. - Select constant (Pn-23 ) (Bias) - Display Pn-23 data. - Change the set value - Write in the set value. (“End is displayed) The data are displayed - Select constant (Pn-23 ) (Bias) - Display Pn-23 data. - Change the set value - Write in the set value. (“End is displayed) The data are displayed | DRIVE PRGM DATA STR RESET DATA STR DATA STR RESET DATA STR DSPL | . Pn-01 Pn-23 0.10 0.00 0.10 Pn-22 1.00 1.23 1.23 | LED DRIVE OFF (10%=0.1) Displayed for 0.5 second. Confirm the display. |

4mA (0V)

16.8mA (0V)

20mA (10V)

10

BIAS

(Pn-23)=0.1

REF. INPUT

LEVEL

100

(Pn-22)= 123

GAIN

GAIN

123

FREQUENCY REFERENCE INPUT

Note: Frequency reference gain (Pn-22) and frequency reference bias (Pn-23) can be changed while running in DRIVE mode.

Note: How to calculate gain

| X = 100−ba … (1) G = 10X+b … (2) X is obtained from equation (1) X = 100−100.8 = 112.5 G is obtained by substituting X obtained in equation (1) to equation (2). G = 112.5 + 10 = 122.5=123 | a: Reference input ratio at 100% frequency since it is 100% speed (60 Hz) at 16.8mA in this example, the following equation is established. 16.8mA−4mA20mA−4mA =0.8a =0.8 b: Bias level (%) Since it is 10% (6Hz) at frequency requence input 4mA in this example, the following equation is established. b = 10 G: gain set value 123 in this example |
| --- | --- |

For instrumentation input of 4 to 20 mA , the amount should be adjusted at startup. Maximum frequency should be adjusted.

Application Example

2.4.2 Calibration of Frequency Meter

Calibration of frequency meter or ammeter connected to the inverter can be performed even without providing a calibration resistor.

<Example>When the frequency meter specifications are 3V

(1mA) full-scale, 3V full-scale output is used at

maximum output frequency [constant (Pn-02)]

operation.Set constant (Pn-45)=0.30.

| Description | Key Operation | Digital Operator Display | Remarks |
| --- | --- | --- | --- |
| - Frequency reference value is displayed. - Select PRGM mode. - Select constant (Pn-45 ) - Display Pn-45 data. - Change the set value - Write in the set value. (“End is displayed) The data are displayed | DRIVE PRGM DSPL DATA STR RESET DATA STR | . Pn-01 Pn-45 0.30 1.00 0.30 | LED DRIVE OFF (Note) Displayed for 0.5 second. Confirm the display. |

Note:

- Since analog monitor gain is set to 1.00 prior shipping, 10V is output at maximum output frequency [constant (Pn-02)] operation.

- By data display of constant (Pn-45) in the program mode, voltage at 100% level according to the constant (Pn-45) set value is output by the meter calibrating function without any conditions.

(Example) Assuming constant(Pn-45)=0.30 : 10V×0.30=3V is output without any conditions.

  - MONITOR FUNCTION

Frequency reference value, output frequency, output current and fault contents can be monitored.

- Typical Monitor Contents and Display (DRV Mode)

DSPL

The monitor item is changed every time the       key is depressed.

Key Operation                                Typical Display

DRV  MODE

Frequency reference value display setting

DSPL

F020.0

Output frequency monitor display

If a fault occurs,

the contents are

displayed.

DSPL

20.0

Output current

monitor display

DSPL

12.5A

Fault reset

RESET

Pn-      display

＊

DSPL

Pn-01

- Monitoring of Fault Contents

RESET

If a fault occurs, the fault conents are displayed with priority over other display items.

Depress the         key or turn on the fault reset input signal (terminal 3 ), to reset the fault.

  - Since the latest fault content data are stored in the inverter, even if the power supply is turned off, they can be monitored after the power supply is turned on again

- Checking fault contents

The latest data are stored in the constant (Pn-48). (except UV)

- Clearing fault contents

The contents are cleared by setting “6” to the constant (Pn-00). Or they are also cleared by constant initialization.

[Set constant (Pn-00)=8 or9.]

At this time, other constants are changed to the factory setting values. Therefore, record all of the constant data before initializing constant.

- Faults to be stored

OC(overcurrent), OV(overvoltage), OH(cooling fin overheat), OL1(motor overload), OL2(inverter overload), OL3(overtorque detection), EF4, EF5(external fault), CPF05(AD converter fault).

For details, refer to Table 1.8 “Fault Display and Contents” on page 27.

  - FUNCTION/CONSTANT LIST

    - A Group Functions(Constant Pn-00 to 19)

| Function | Pn- | Name | Description |  |  |  |  | Initial Setting | User Set Values | Ref. Par. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Display of Operator | 00 | Constant Group Selection | 0:A group function constant(Pn-01~19) are locked(can be read only). Pn-00 can be set/read. 1:A group function constant(Pn-00~19)can be set/read 2.A,B group function constant(Pn-00~29)can be set/read. 3.A,B,C group function constant(Pn-00~59) can be set/read. |  |  |  |  | 1 |  | 2.7.1 |
|  |  | Fault Contents Clear | 6:Fault record clear |  |  |  |  |  |  |  |
|  |  | Constant Initialization | 8:Inittalize(multifunction terminal:initial value setting) 9:Initalize (3-wire sequence) |  |  |  |  |  |  |  |
| Run Stop Signal Selection 1 | 01 (Note 1) | Operation Method Selection | 4 | 3 | 2 | 1 | Master frequency Reference-Control circuit terminals 8 and 11, or 9 and 11 inputs | 0011 (0000) (Note2) |  | 2.7.2 |
|  |  |  | - | - | - | 0 |  |  |  |  |
|  |  |  | - | - | - | 1 | Master frequency reference-Operator FXXXX |  |  |  |
|  |  |  | - | - | 0 | - | Run by control circuit terminal run command |  |  |  |
|  |  |  | - | - | 1 | - | Run by operator run command |  |  |  |
|  |  | Stopping Method Selection | - | 0 | - | - | Deceleration to stop |  |  |  |
|  |  |  | - | 1 | - | - | Coasting to stop |  |  |  |
| Output Voltage Limiter Selection |  | V/f Pattern Setting | 0 | - | - | - | Free choice V/f with output voltage limiter |  |  |  |
|  |  |  | 1 | - | - | - | Free choice V/f without output voltage limiter |  |  |  |

Note:

1.The first four digits indicated in the description of constant (Pn-01) mean the following digits. This also applies to the other constants.

0  0  0  0

1st digit

2nd digit

3rd digit

4th digit

2.The value is factory set value of models with analog operator.

| Function | Pn- | Name | Description | Initial Setting | User Set Values | Ref. Par |
| --- | --- | --- | --- | --- | --- | --- |
| V/f Pattern Setting | 02 | Maximum Output Frequency | Setting unit:0.1 Hz Setting range:50.0 to 400.0Hz | 60.0Hz |  | 2.7.3 |
|  | 03 | Maximum Voltage | Setting unit:0.1Hz Setting range:0.1 to 255.0V | 220V (Note 1) |  |  |
|  | 04 | Maximum Voltage Output Frequency (Base Frequency | Setting unit:0.1Hz Setting range:0.2 to 400.0Hz | 60.0Hz |  |  |
|  | 05 | Intermediate Output Frequency | Setting unit:0.1Hz Setting range:0.1 to 399.9 Hz | 1.5Hz |  |  |
|  | 06 | Intermediate Output Frequency Voltage | Setting unit:0.1 V Setting range:0.1 to 255.0V | 13.2V (Note 1) |  |  |
|  | 07 | Minimum Output Frequency | Setting unit:0.1Hz Setting range:0.1 to 10Hz | 1.5Hz |  |  |
|  | 08 | Minimum Output Frequency Voltage | Setting unit:0.1 V, Setting range:0.1 to 50V | 13.2V (Note 1) |  |  |
| First Accel/Decel Time Setting | 09 | Acceleration Time 1 | Setting unit:0.1s, Setting range:0.0 to 600.0s | 10.0s |  | 2.7.4 |
|  | 10 | Deceleration Time 1 | Setting unit:0.1s, Setting range:0.0 to 600.0s | 10.0s |  |  |
| Second Accel/Decel Time Setting | 11 | Acceleration Time 2 | Setting unit:0.1s, Setting range:0.0 to 600.0s | 10.0s |  |  |
|  | 12 | Deceleration Time 2 | Setting unit:0.1s, Setting range:0.0 to 600.0s | 10.0s |  |  |

Note:1. For 440 V class, the value is twice as that of 220 V class.

| Function | Pn- | Name | Description |  |  |  |  | Initial Setting | User Set Values | Ref. Par. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Frequency Reference (Note 1) | 13 | Frequency Reference 1 | Setting unit:0.1 Hz, Setting range:0.0 to 400.0 Hz |  |  |  |  | 0.0Hz |  | 2.7.5 |
|  | 14 | Frequency Reference 2 | Setting unit:0.1 Hz, Setting range:0.0 to 400.0 Hz |  |  |  |  | 0.0Hz |  |  |
|  | 15 | Frequency Reference 3 | Setting unit:0.1 Hz, Setting range:0.0 to 400.0 Hz |  |  |  |  | 0.0Hz |  |  |
|  | 16 | Frequency Reference 4 | Setting unit:0.1 Hz, Setting range:0.0 to 400.0 Hz |  |  |  |  | 0.0Hz |  |  |
|  | 17 | Jog Frequency Reference | Setting unit:0.1 Hz, Setting range:0.0 to 400.0 Hz |  |  |  |  | 6.0Hz |  | 2.7.6 |
| Electronic Thermal Overload Motor Protection | 18 | Motor Protection Selection | 4 | 3 | 2 | 1 | Electronic thermal overload motor protection provided | 0000 |  | 2.7.7 |
|  |  |  | - | - | - | 0 |  |  |  |  |
|  |  |  | - | - | - | 1 | Electronic thermal overload motor protection not provided |  |  |  |
|  |  |  | - | - | 0 | - | Electronic thermal overload characteristics is for standard motor |  |  |  |
|  |  |  | - | - | 1 | - | Electronic thermal overload characteristics is for constant torque motor |  |  |  |
|  |  |  | - | 0 | - | - | Electronic thermal overload time constant is of standard rating |  |  |  |
|  |  |  | - | 1 | - | - | Electronic thermal overload time constant is of short-term rating |  |  |  |
|  |  |  | 0 | - | - | - | Not used |  |  |  |
|  |  |  | 1 | - | - | - |  |  |  |  |
| Electronic Thermal Overload Reference Current | 19 | Motor Rated Current | Setting unit :0.1A, Setting range: 10 to 120% of inverter rated current |  |  |  |  | 3.3A (Note2) |  | 2.7.7 |

Note:1 Can be changed even during run.

The maximum setting frequency to be set to frequency reference is the maximum frequency(Pn-02).

2. Initial setting differs according to the inverter capacity. The values in the above list are provided when model JNTABDCB0001 JK--- and TECO standard motor 220V 60Hz 4 poles 1HP(0.75kw) are combined.

    - B Group Functions(Constant Pn-20 to 29)

| Function | Pn- | Name | Description |  |  |  |  | Initial Setting | User Set Values | Ref. Par. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Run Signal Selection 2 | 20 | REV Run Prohibit | 4 | 3 | 2 | 1 | REV run enabled | 0000 |  | 2.7.2 |
|  |  |  | - | - | - | 0 |  |  |  |  |
|  |  |  | - | - | - | 1 | REV run disabled |  |  |  |
|  |  | Operator Stop Key Precedence | - | - | 0 | - | STOP key effective from control circuit terminals during run |  |  | - |
|  |  |  | - | - | 1 | - | STOP key ineffective from control circuit terminals during run |  |  |  |
|  |  | Output Frequency UP/DOWN operation | - | 0 | - | - | Change the frequency reference by Increament or Decreament key,after depress the STR key, the output frequency starting to up or down |  |  | 2.7.25 |
|  |  |  | - | 1 | - | - | The output frequency can be up or down by Increament or Decerament key, directly. |  |  |  |
|  |  | Stall Prevention During Deceleration | 0 | - | - | - | Stall prevention during deceleration provided |  |  | 2.7.14 |
|  |  |  | 1 | - | - | - | Stall prevention during deceleration not provided(when braking resistor connected) |  |  |  |
| Analog Monitor Selection | 21 |  | - | - | - | 0 | Not used | 0000 |  | 2.7.8 |
|  |  |  | - | - | - | 1 |  |  |  |  |
|  |  | Output Monitor Selection (Note 1) | - | - | 0 | - | Analog monitor output frequency |  |  |  |
|  |  |  | - | - | 1 | - | Analog monitor output current |  |  |  |
|  |  | S-curve Accel/decel Selection | 0 | 0 | - | - | Not provided |  |  | 2.7.9 |
|  |  |  | 0 | 1 | - | - | 0.2 Sec |  |  |  |
|  |  |  | 1 | 0 | - | - | 0.5 Sec |  |  |  |
|  |  |  | 1 | 1 | - | - | 1.0 Sec |  |  |  |

Note:1. Analog monitor gain is set by constant Pn-45.

| Function | Pn- | Name | Description | Initial Setting | User Set Values | Ref. Par. |
| --- | --- | --- | --- | --- | --- | --- |
|  | 22 | Frequency Reference Gain | Setting unit: 0.01, Setting range: 0.01 to 2.00 | 1.00 |  | 2.7.10 |
|  | 23 | Frequency Reference Bias | Setting unit: 0.01, Setting range:-1.00 to 1.00 | 0.00 |  |  |
| Frequency Limit Control | 24 | Frequency Upper Limit | Setting unit: 1%, Setting range: 0 to 110% | 100% |  | 2.7.11 |
|  | 25 | Frequency Lower Limit | Setting unit: 1%, Setting range: 0 to 110% | 0% |  |  |
| DC Injection Braking | 26 | DC Injection Braking Current | Setting unit: 1%, Setting range:0 to 100% of inverter rated current | 50% |  | 2.7.12 |
|  | 27 | DC Injection Braking Time at Stop | Setting unit:0.1s, Setting range:0.0 to 5.0s | 0.5s |  |  |
|  | 28 | DC Injection Braking Time at Start | Setting unit:0.1s, Setting range:0 to 5.0s | 0.0s |  |  |
| Torque Compen- sation | 29 | Automatic Torque Boost Gain | Setting unit:0.1, Setting range:0.0 to 3.0 | 1.0 |  | 2.7.13 |

    - C Group Functions (Constant Pn-30 to 59)

| Function |  | Pn- | Name | Description | Initial Setting | User Set Values | Ref. Par. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Stall Prevention |  | 30 | Level of Stall Preventive Operation during Acceleration | Setting unit:1%, Setting range:30 to 200%of inverter rated current | 170% (Note 1) |  | 2.7.14 |
|  |  | 31 | Level of Stall Preventive Operation during run | Setting unit:0% Setting range:30 to 200%of inverter rated current | 160% (Note 2) |  |  |
| Multifunction Selection | Contact Input Signal | 32 | Multifunction Input Selection 1 (Terminal 4 Function Selection | 0:FWD/REV run command(3-wire sequence selection) 1:External fault(No contact input) 2: External fault(NC contact input) 3:Multi-step speed reference 1 4:Multi-step speed reference 2 5:JOG command 6:Accel/decel time select 7:External baseblock(No contact input) 8: External baseblock(NC contact input) 9:Search command from maximum frequency 10: Search command from setting frequency 11:Accel/decel prohibit | 1 |  | 2.7.15 2.7.25 |
|  |  | 33 | Multifunction Input Selection 2 (Terminal 5 Function Selection) | 1:External fault(No contact input) 2: External fault(NC contact input) 3:Multi-step speed reference 1 4:Multi-step speed reference 2 5:JOG command 6:Accel/decel time select 7:External baseblock(No contact input) 8: External baseblock(NC contact input) 9:Search command from maximum frequency 10: Search command from setting frequency 11:Accel/decel prohibit | 3 |  |  |

Note:1. Stall prevention during acceleation does not operate at 200%.

2. Stall prevention during run does not operate at 200%.

| Function |  | Pn- | Name | Description |  |  |  |  | Initial Setting | User Set Values | Ref. Par. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Photo Coupler Output Signal | 34 | Multifunction Output Selection 1 (Terminal 13 Function Selection) | 0:Running 1:Frequency agreement 2:Zero speed 3:Frequency detection (output frequency≧frequency detection level) 4:Overtorque detection |  |  |  |  | 0 |  | 2.7.16 2.7.17 |
|  |  | 35 | Multifunction Output Selection 2 (Terminal 14 Function Selection) | 0:Running 1:Frequency agreement 2:Zero speed 3:Frequency detection (output frequency≧frequency detection level) 4:Overtorque detection |  |  |  |  | 1 |  |  |
| Desired Speed Detection |  | 36 | Frequency Detection Level | Setting unit:0.1 Hz, Setting range:0.0 to 400.0Hz |  |  |  |  | 0.0Hz |  | 2.7.17 |
| Over- torque Detection |  | 37 | Overtorque Detection Function Selection | 4 | 3 | 2 | 1 | Overtorque detection not provided | 0000 |  | 2.7.18 |
|  |  |  |  | - | - | - | 0 |  |  |  |  |
|  |  |  |  | - | - | - | 1 | Overtorque detection provided |  |  |  |
|  |  |  |  | - | - | 0 | - | Detected only frequency agreement |  |  |  |
|  |  |  |  | - | - | 1 | - | Detected during running |  |  |  |
|  |  |  |  | - | 0 | - | - | Operation continues after overtorque |  |  |  |
|  |  |  |  | - | 1 | - | - | detection output shut-off at overtorque detection |  |  |  |
|  |  |  |  | 0 | - | - | - | Not used |  |  |  |
|  |  |  |  | 1 | - | - | - |  |  |  |  |
|  |  | 38 | Overtorque Detection Level | Setting unit:1%, Setting range: 30 to 200% of inverter rated current |  |  |  |  | 160% |  |  |
|  |  | 39 | Overtorque Detection time | Setting unit:0.1s, Setting range:0.1 to 10.0s |  |  |  |  | 0.1s |  |  |

| Function | Pn- | Name | Description |  |  |  |  | Initial Setting | User Set Values | Ref. Par. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Carrier Frequency Adjustment | 40 | Carrier Frequency | Setting unit: 1(2.5kHz) Setting range:1 to 6(2.5 to 15kHz) |  |  |  |  | 4 (10kHz) |  | 2.7.19 |
| - | 41 to 44 | Not used | (Setting disabled) |  |  |  |  | - |  |  |
| Analog Monitor Scale Calibration | 45 | Analog Monitor Gain | Setting unit:0.01, Setting range:0.01 to 2.00 |  |  |  |  | 1.00 |  | 2.7.20 |
| Momentary Power Loss Protection | 46 | Operation Selection after Momentary Power Loss | 4 | 3 | 2 | 1 | Continuous operation after momentary power loss not provided | 0000 |  | 2.7.21 |
|  |  |  | - | - | - | 0 |  |  |  |  |
|  |  |  | - | - | - | 1 | Continuous operation after momentary power loss provided |  |  |  |
|  |  |  | 0 | 0 | 0 | - | Not used |  |  |  |
| Fault Retry | 47 | Fault Retry Selection | Setting unit:1 time Setting range:0 to 10 times Note: By setting 0 times, fault retry function becomes disabled. |  |  |  |  | 0 |  | 2.7.22 |
| Fault Trace | 48 | Fault Record | The latest fault is displayed(setting disabled). |  |  |  |  | - | - | - |
| Software Version | 49 | PROM No. | PROM No. is displayed (setting disabled). |  |  |  |  | - | - | - |
| Frequency Jump Control | 50 | Jump Frequency 1 | Setting unit:0.1Hz, Setting range:0.0 to 400.0Hz |  |  |  |  | 0.0Hz |  | 2.7.23 |
|  | 51 | Jump Frequency 2 | Setting unit:0.1Hz, Setting range:0.0 to 400.0Hz |  |  |  |  | 0.0Hz |  |  |
|  | 52 | Jump Frequency 3 | Setting unit:0.1Hz, Setting range:0.0 to 400.0Hz |  |  |  |  | 0.0Hz |  |  |
|  | 53 | Jump Frequency Width | Setting unit:0.1Hz, Setting range:0.0 to 25.5Hz |  |  |  |  | 1.0Hz |  |  |

| Function | Pn- | Name | Description | Initial Setting | User Set Values | Ref. Par |
| --- | --- | --- | --- | --- | --- | --- |
| Speed Search Control | 54 | Speed Search Operation Level | Setting unit:1%, Setting range: 0 to 200% of inverter rated current | 150% |  | 2.7.21 2.7.22 2.7.24 |
|  | 55 | Minimum Baseblock Time | Setting unit:0.1s, Setting range:0.5 to 5.0s | 0.5s |  |  |
|  | 56 | V/f during Speed Search | Setting unit:1%, Setting range: 0 to 100% | 100% |  |  |
| - | 57 to 59 | Not Uesd | (Setting disabled.) | - |  | - |

  - DESCRIPTION OF FUNCTIONS AND CONSTANTS

The following describes the functions and constants set by digital operator, Constant Pn-□□ are indicated as

    - DISPLAY OF  OPERATOR

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| Constant Group Selection |  | 1 |

˙  =0    The A group functions:

        - can be set and read.

0 - 19 can be read only, This setting prevents constant from being reset by improper operation after completion of constant setting.

˙  =1     The A group functions ( 0 to 19 ) can be set and read.

˙  =2     The A and B group functions (0 to 29 )can be set and read

˙  =3     The A,B and C group functions ( 0 to 59 ) can be set and read.

˙  =6     Fault history is cleared.

˙  =8     All control constants can be initialized. Terminal functions are retuned to the factory setting.

˙  =9    All control constants can be initialiaed. Therminal functions are of 3-wire sequence. Refer to “MULTIFUNCTION CONTACT INPUT FUNCTION SELECTION” onpage 84

    - RUN˙STOP  PROCEDURE SELECTION

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| Start/Stop Procedure | 1 | 0011(0000)* |
| Reverse Rotation Prevention | 20 | 0000 |

*The value in parentheses is factory setting of models with analog operator (JNEP- -14)

- Start procedure

Operation can be performed from the operator or control circuit terminal input.

1 =  X  X  0  0  (X means 1 or 0 )

1st digit

0: Frequency reference from control circuit terminal

1: Frequency reference from the operator.

2nd digit

0: Start/stop control from control circuit terminal

1: Start/stop control from the operator.

- Stop procedure

Stopping mode can be selected according to the application.

1 =  X  0  X  X

3rd digit

0:Deceleration to stop

1:Coasting to stop.

- Reverse rotation

Prevents accidental selection of reverse rotation.

Reverse run command is disregarded if input

20 = X  X  X  1

1st digit

0: Reverse rotation is possible

1: Reverse rotation is impossible.

    - V/f CHARACTERISTIC SETTING

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| Max. Output Frequency | 2 | 60.0Hz |
| Max. Voltage | 3 | 220.0V |
| Max. Voltage Output Frequency | 4 | 60.0Hz |
| Intermediate Output Frequency | 5 | 1.5Hz |
| Intermediate Output Frequency Voltage | 6 | 13.2V |
| Min. Output Frequency | 7 | 1.5Hz |
| Min. Output Frequency Voltage | 8 | 13.2V |
| Output Voltage Limiter Selection | 1 | 0000 |

- V/F pattern setting

Any desired v/f pattern can be set for special specifications, too. Any v/f pattern can be set according to the load characterics. The factory preset value is set to

60 Hz saturation type pattern.

V

V

Vmax. (Pn-03)

Vmax. (Pn-03)

VC.  (Pn-06)

Vmin. (Pn-08)

Vmin. (Pn-08)

.  (Pn-06)

F

F

Fmin.
(Pn-07)

FB
(Pn-05)

FA
(Pn-04)

Fmax.
(Pn-02)

(120 Hz)

Fmin.
(Pn-07)

Fmax.
(Pn-02)

(120 Hz)

(Pn-05)

(Pn-04)

Note:  1.If an excessively large value is set in low-speed area (3 Hz or less), motor overheat or inverter malfunction may occur. Change the constant gradually monitoring load or motor current.

2.The v/f constants setting have to be satisfied as following conditions:

Max. output frequency (Pn-02)≧Max. voltage frequency (Pn-04) ＞           Intermediate output frequency (Pn-05)≧Min. output frequency (Pn-07)

3.For the following setting, intemediate output frequency voltage (Pn-06) is disregarded:

Intermediate output frequency (Pn-05) = Min. output frequency (Pn-07)

˙Output limiter selection

When v/f is set to excessively large value, an inverter fault may occur. Therefore, in order to prevent the malfunction, the upper limit is provided for the output voltage. However, the setting is not necessary under normal operation.

1 =  0  X  X  X

4th digit

0: Desired v/f with output voltage limiter

1: Desired v/f without output voltage limiter

output voltage limit pattern (Note)

250v

40v

5v

F

0     Pn-04 /40      Pn-04

Note: For 440 v class, the value is twice that of 220 v class.

If “1” is set, v/f matching the motor characteristics must be selected.

    - ACCEL / DECEL TIME SETTING

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| Acceleration Time 1 | 9 | 10.0s |
| Deceleration Time 1 | 10 | 10.0s |
| Acceleration Time 2 | 11 | 10.0s |
| Deceleration Time 2 | 12 | 10.0s |
| Accel/Decel Time Select | 32 , 33 | See page 63. |

˙Each item can be set from 0.0 sec to 600 sec.

The set time indicates the interval required before the maximum output freqnency setting Pn-02 is reached.

Accel/decel time can be set for two-step switching using multifunction contact input (control circuit terminals 4 or 5 ), even during running.

Between control circuit terminals 4 or 5.

˙open : Pn-09 and Pn-10 are selected.

˙closed : Pn-11 and Pn-12 are selected

(When setting = 6 )

Output Frequency

Pn-11

Pn-12

Pn-02

Pn-09

Pn-10

Time

Note: S-curve accel/decel reducing shock at motor starting is also enabled. When S-curve accel/decel is needed, refer to “S-CURVE PATTERN SELECTION” on page 77.

2.7.5  4-STEP SPEED CHANGE

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| Multi-speed Frequency Reference | 13 to 16 | See page 60. |
| Multi-speed Operation Function | 32 , 33 | See page 63. |

Up to 4 steps of speed can be set by contact input by setting 4 and 5  multi-speed references

To multi-function contact input terminals.

This eliminates the need for an analog signal thereby enabling operation even at low speed without being affected by noise. See the following example.

˙Set according to run specifications.

FREQ REF.4

Fref

FREQ. REF.3

FREQ. REF.2

(Pn-16)

FREQ REF.1

(Pn-15)

(Pn-13)

(Pn-14)

t

0

closed

TERMINAL

FWD RUN COMMAND    1

open

REVRUN COMMAND     2

MULTI-STEP SPEED        4

REFERENCE 1

MULTI-STEP SPEED        5

REFERENCE 2

Note: 1. Frequency reference can be changed only if it is selected by multi-speed reference.

2.The following condition must be satisfied :

Set frequency reference(Pn-13 to 16) ≦ Max. output frequency (Pn-02) ×

output frequency upper limit value (Pn-24)

    - JOG OPERATION

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| Jog Frequency Reference Setting | 17 | 6.0Hz |
| Jog Reference Selection | 32 , 33 | See page 63. |

Select the JOG mode ( closed between terminals 4 to 6 ) and JOG operation can be performed by FWD/REV run command (when setting Pn-32 = 5 )

Depressing the JOG key on the digital operator performs the same operation.

Fref

Pn-17

TERMINAL

t

MULTI-STEP SPEED        4

REFERENCE 1

ON

ON

FWD RUN COMMAND    1

ON

REVRUN COMMAND     2

Note: The following condition must be satistied in the jog frequency reference setting.

JOG frequency reference (Pn-17) ≦ Max. output frequency (Pn-02) ×

output frequency upper limit value (Pn-24)

    - ELECTRONIC THERMAL OVERLOAD FUNCTION

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| Motor Type | 18 | 0000 |
| Motor Rated Current | 19 | 3.3 A (Note) |

Motor output current is detected by the inverter built-in electrical thermal overload function, and inverter exclusive use motor or standard motors are prevented from overloading. (It is not necessary to mount the thermal relay externally. However, to connect several motors to one inverter, a thermal overload relay must be inserted for each motor. It is necessary to reduce carrier frequency according to the wiring distance between the inverter and motor when thermal overload relays are inserted. For details, refer to the precautions on wiring described on page 12)

Pn-19 = Motor rated current value

Set the motor rated current value according to the value on the motor nameplate.

Pn-18 = X  0  0  0

|  | Electronic thermal motor protection |
| --- | --- |
| 0 | Effective |
| 1 | Ineffective |

|  | Electronic thermal characteristics |
| --- | --- |
| 0 | For standard motor |
| 1 | For constant torque motor |

|  | Electronic thermal time constant |
| --- | --- |
| 0 | For standard motor and constant torque motor |
| 1 | For motor other than listed in 0 above. (Short time rating) |

˙The electronic thermal overload function is depended on the motor overload protection start current (ie. Motor rated current). The setting range is 10~120% of inverter rated current. The standard set value for each capacity has already set at factory as following. If the general-purpose motor rated current value is different from the standard value, change the setting.

˙220V Class Common in 3-phase and Single-phase Series

| Model | 3-phase JNTABDCB JK--- | R500 | 0001 | 0002 | 0003 | 0005 | 7R50 | 0010 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Single-phase JNTBBDCB JK--- |  |  |  |  |  |  |  |
| Max. Applicable HP Motor Capacity (KW) |  | 0.5 (0.4) | 1 (0.75) | 2 (1.5) | 3 (2.2) | 5 (3.7) | 7.5 (5.5) | 10 (7.5) |
| Motor Current Value at Factory Setting (A) |  | 2.1 | 3.3 | 6.4 | 8.6 | 13.5 | 20.1 | 25.1 |

˙440V Class 3-phase Series

| Model JNTABDCB AZ---- | R500 | 0001 | 0002 | 0003 | 0005 | 7R50 | 0010 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Max. Applicable HP Motor Capacity (KW) | 0.5 (0.4) | 1 (0.75) | 2 (1.5) | 3 (2.2) | 5 (3.7) | 7.5 (5.5) | 10 (7.5) |
| MotorCurrent Value at Factory Setting (A) | 1.0 | 1.7 | 2.9 | 4.1 | 6.8 | 10.1 | 12.6 |

Note: The motor current value at factory setting is according to TECO standard 4-pole motor.

    - MULTIFUNCTION ANALOG OUTPUT MONITOR SETTING

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| Output Monitor Select | 21 | 0000 |
| Analog Monitor Gain | 45 | 1.00 |

Either output frequency or output current can be monitored by analog output between control circuit terminals 12 and 11. ( 0 to 10V output)

Pn-21 = X  X  0  X

Not used

Output contents between control circuit terminals 12 to 11

2nd digital

0: Output frequency monitor

1: Output current monitor

Analog output monitor gain can be set by Pn-45.

Additionally, analog output monitor voltage is output as show below :

Output frequency monitor:

Output voltage (v)

= output frequency × 10 ÷ Max. output frequency (Pn-02) × (Pn-45)

Output current monitor:

Output voltage (v)

= output current × 10 ÷ Inverter rated current  × (Pn-45)

Note: Since output current becomes approx. 200% maximum of the inverter rated current, output voltage is clamped at approx. 11v when Pn-45 is used at 1.00 and the inverter rated current is exceeded. To keep linearity, set Pn-45 to approx. 0.5 .

    - S-CURVE PATTERN SELECTION

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| S-curve Pattern Selection | 21 | 0000 |

To prevent shock at machine starting/stopping, accel/decel S-curve pattern is enabled by the setting of Pn-21.

Pn-21 = 0  0  X  X

| 4th digit | 3rd digit | Contents |
| --- | --- | --- |
| 0 0 1 1 | 0 1 0 1 | No S-curve characteristics. The S-curve characteristics is 0.2 second. The S-curve characteristics is 0.5 second. The S-curve characteristics are 1 second. |

OUTPUT FREQUENCY

FREQUENCY  REF.

TIME

S-CURVE CHARACTERISTICS TIME (TSC)

Note: S-curve characteristics time refers to the time from acceleration rate 0 to the time when a normal acceleration rate determined by a specified acceleration time is obtained.

The figure below shows the time chart at FWD/REV run change during deceleration and stop.

FWD RUN

COMMAND

REV RUN

COMMAND

ACCELER-

ATION

DECELER-

ATION＊

DC INJECTION BRAKINC TIME

AT STOPPING

(Cn-12)

ACCELERATION

OUTPUT FREQUENCY

MIN. OUTPUT FREQUENCY

(Cn-07)

:   S-CURVE CHARACTERISTIC

DC INJECTION BRAKINC START FREQUENCY (Cn-10)

MIN. OUTPUT FREQUENCY

(Cn-07)

DECELER-

ATION＊

    - FREQUENCY COMMAND GAIN/BIAS

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| Frequency Reference Gain | 22 | 1.00 |
| Frequency Reference Bias | 23 | 0.00 |

Output frequency (gain/bias) can be set freely according to frequency setting ( 0 to 10 v

Or 4 to 20 mA).

Fref [Hz]

Pn-02 * Pn-22

100%

BIAS

Pn-02 * Pn-23

SET FREQUENCY REF.

10 v

(20mA)

0

(4mA)

For the setting method, refer to Par.2.4.1  “ Output Frequency Bias (Pn-23) and Gain (Pn-22)”

On page 53.

    - OUTPUT FREQUENCY LIMIT

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| Output Frequency (Speed) Upper Limit | 24 | 100% |
| Output Frequency (Speed) Lower Limit | 25 | 0 |

The upper and lower limits for the output frequency can be set. When the lower limit is not 0, acceleration to that lower limit setpoint begins until frequency reference reaches the lower limit value when the start command is input.

Output Fref [Hz]

FREQUENCY REF. UPPER LIMIT         Pn-24

FREQUENCY REF. LOWER LIMIT          Pn-25

0

100%

FREQUENCY COMMAND

Note: By setting Pn-24 to 110%, frequency up to Pn-02 x 1.1 can be output.

(Example) Assuming Pn-02 = 60.0Hz, Pn-24 = 1.1, up to 66Hz can be output. However, when the frequency exceeds 400Hz, it is clamped at 400Hz.

    - DC INJECTION BRAKING

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| DC Injection Braking during Stop | 27 | 0.5s |
| DC Injection Braking at Start | 28 | 0.0s |
| DC Injection Braking Current | 26 | 50% |

˙DC injection braking at stop

Prevents overrun at stop.

frequency

If output frequency becomes

Minimum output frequency

Pn-07

time

Pn-07 or less, DC injection brake

current

is applied for the time set by Pn-27,

and the motor is stopped. By setting

Pn-26

time

0s to Pn-27, DC injection braking

Pn-27

becomes disable: the motor coast to

frequency

stop when the output frequency is

less than the minmum output

Pn-07

frequency Pn-07.

time

current

Pn-26

time

˙DC injection braking at start

Starts a coasting motor without tripping even when the direction of  rotation is unknown. When the run command is input, DC injection brake is applied for the time set by   , and the motor stops. Then the motor starts operation.

˙DC braking current

DC injection braking current 100% equals the inverter rated current. It is set to 50% at factory prior to shipping.

    - FULL-RANGE AUTOMATIC TORQUE BOOST

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| Torque Compensation Gain | 29 | 1.0 |

Automatic control of V/f ratio according to the load torque ensures tripless operation and optimum output current. Therefore, tripless operation with excellent energy-saving effect is available. When the wiring distance between the inverter and motor is long (normally approx. 100m) and when the motor torque is a little short, increase torque compensation gain gradually, checking the motor current. Normally, no adjustment is necessary.

OUTPUT

TORQUE INCREASE

VOLTAGE  100%

TORQUE DECREASE

NORMAL FREQUENCY

2.7.14 MOTOR STALL PREVENTION FUNCTION

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| Operation Level for Stall Prevention during Acceleration | 30 | 170% |
| Operation Level for Stall Prevention during Running | 31 | 160% |
| Stall Prevention Function during Deceleration | 20 | 0000 |

Automatically adjusts output frequency according to the load so as to continue operation of the machine without stalling the motor.

˙Stall prevention during acceleration.

If the motor current exceeds the value set to Pn-30 during acceleration, accleration is stopped until the motor current is reduced to the Pn-30 set value or less.

Motor current

Pn-30

Time

Output frequency

Time

˙Stall prevention during running

If the motor current exceeds the value set to   because of impact load during running, output frequency is automatically lowered. When the motor current is reduced to the  set value or less, the motor starts acceleration again and the operation is continued.

Motor current

Pn-31

Time

Output frequency

Time

˙Stall prevention during deceleration

Automatically adjusts deceleration rate with monitoring DC voltage to prevent overvoltage during deceleration. Set “1” for connecting braking resistor.

Pn-20 =  0  X  X  X

4th digit

0: Stall prevention during deceleration enabled.

1: Stall prevention during deceleration disabled.

˙When the motor load is large or accel/decel time is short, the accel/decel time may be longer than the set value because of the stall preventive function.

    - ULTIFUNCTION CONTACT INPUT FUNCTION SELECTION

| Item Name | Constant to be set | Factory PRESET |
| --- | --- | --- |
| Multifunction Contact Input Function | 32 , 33 | Refer to page 63 |

The function of control circuit terminals 4 and 5 can be changed if necessary.

Set Pn-32 and Pn-33 in the descending order.

Pn-32 set value ＜ Pn-33 set value

Terminal 4 function: Set to Pn-32

| Set Value | Function | Page |
| --- | --- | --- |
| 0(Note) | FWD/REV run command (3-wire sequence selection) | ˍ |
| 1 | External fault (NO contact input | 101 |
| 2 | External fault (NC contact input) | 101 |
| 3 | Multi-step speed reference 1 | 72 |
| 4 | Multi-step speed reference 2 | 72 |
| 5 | JOG command | 73 |
| 6 | Accel/decel time select | 71 |
| 7 | External baseblock (NO contact input) | 107 |
| 8 | External baseblock (NC contact input) | 107 |
| 9 | Search command from maximum frequency | 96 |
| 10 | Search command from setting frequency | 96 |
| 11 | Accel/decel prohibit command | 98 |

Note: Terminal function at 3-wire sequence selection.

7200M3

STOP

RUN

RUN COMMAND (RUNS WHEN "CLOSED")

1

2

STOP COMMAND (STOPS WHEN "OPEN")

FWD/REV RUN SELECT

4

"OPEN": FWD RUN

"CLOSED": REV RUN

6

Terminal 5 function: Set to Pn-33

| Set Value | Function | Page |
| --- | --- | --- |
| 1 | External fault (NO contact input) | 101 |
| 2 | External fault (NC contact input) | 101 |
| 3 | Multi-step speed reference 1 | 72 |
| 4 | Multi-step speed reference 2 | 72 |
| 5 | JOG command | 73 |
| 6 | Accel/decel time select | 71 |
| 7 | External baseblock (NO contact input) | 107 |
| 8 | External baseblock (NC contact input) | 107 |
| 9 | Search command from maximum frequency | 96 |
| 10 | Search command from settingfrequency | 96 |
| 11 | Accel/decel prohibit command | 98 |

˙Contact input capacity is 24 Vdc 8mA or less.

˙Circuit leakage current at signal OFF must be 100μA or less.

Wiring example (Open-collector input)

Note: When the multifuntion contact input is selected as JOG command, the Jog frequency.

    - MULTIFUNCTION PHOTO- COUPLER OUTPUT FUNCTION SELECTION

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| Multifunction Contact Output Fubction | 34 , 35 | See page 64 |

Functions of control circuit terminals 13 - 7 , and 14 - 7 , can be switched.

Function of terminal between 13 - 7 at “L” :Set into Pn-34 .

Function of terminal between 14 - 7 at “L” :Set into Pn-35 .

| Set Value | Function |
| --- | --- |
| 0(Note 1) | Running |
| 1(Note 2) | Frequency agreed |
| 2 | Zero speed |
| 3 | Frequency detection (output frequency ≧frequency detection level) |
| 4 | Overtorque detected |

Note: 1. Factory preset value of  .

2. Factory preset value of  .

˙ Maximum output capacity is 48 VDC 50mA.

˙  To drive an inductive load, be sure to insert a free-wheel diode to control surge voltage.

    - SPEED AGREED SIGNAL OUTPUT

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| Frequency Detection Level | 36 | 0.0 Hz |
| Multifunction Contact Output Function | 34 , 35 | See page 64 |

This function is used when operation at an arbitrary speed must be indicated. By setting either set value to multifunction contact output function ( Pn-34 , Pn-35 ) the following signal output to control circuit terminal 13 or 14 is enabled. Set 1 or 3 to Pn-34 or Pn-35 when the signal is to be output to control circuit terminals 13 and 14 , respectively.

(1) Set value = 1 : frequency agreed

DETECTION WIDTH  ±2Hz

FREQUENCY REF.

OUTPUT FREQUENCY

AGREED FREQUENCY SIGNAL

CLOSED

(2) Set value = 3 : output frequency ≧ frequency detection level

Pn-36

OUTPUT FREQUENCY

FREQUENCY DETECTION SIGNAL

CLOSED

However, When “frequency agreed” is selected, the frequency agreed signal is turned OFF immediately at stop signal input.

DETECTION WIDTH ±2Hz

OUTPUT FREQUENCY

CLOSED

RUN SIGNAL

FREQUENCY AGREED

SIGNAL

    - OVERTORQUE DETECTION FUNCTION

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| Overtorque Detection Level | 38 | 160% |
| Overtorque Detection Time | 39 | 0.1s |
| Overtorque Detection Signal | 34 , 35 | See page 64 |
| Overtorque Detection Selection | 37 | 0000 |

When excess load is placed on machine, the increase in motor current is detected. If current exceeding the value set by Pn-38 lasts for a time exceeding the value set by Pn-39, the overtorque detected signal is output to control circuit terminal 13 or 14 until the current reduced to the Pn-38 set value or less. To output the signal to control circuit terminal 13 , set Pn-34 to 4, and to 14, Pn-35 to 4.

MOTOR CURRENT

Pn-38

HYSTERESIS 5%

TIME

MULTI-FUNCTION OUTPUT SIGNAL

(OVERTORQUE DETECTION SIGNAL)

ON

ON

Pn-39

Pn-39

The Pn-37 setting can select overtorque detection only during agreed speed or during running

Additionally, it can select continuous operation or output shut-off at overtorque detection.

Pn-37 = X  0  0  X

2nd digit

0:Overtorque is detected only during agreed frequency.

1:Overtorque is detected during running except for DB.

3rd digit

0: When overtorque is detected, the operation continues.

1: When overtorque is detected, the inverter output is shut OFF.

Fault contact signal is output. (Treated as a fault)

    - CARRIER FREQUENCY SETTING

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| Carrier Frequency | 40 | 4 |

Changing the carrier frequency reduces RFI noise and leakage current without increasing motor noise.

Carrier frequency (kHz)=2.5kHz ×Pn-40 set value

| 1 | 2 | 3 | 4* | 5 | 6 |
| --- | --- | --- | --- | --- | --- |

*Factory preset value

CARRIER FREQUENCY

HIGH

LOW

METALLIC NOISE

FROM MOTOR

(RATHER HIGH)              (NOT AUDIBLE)

Note: Reduce continuous output current for changing the set value to 5 or 6.

| Carrier Frequency Set Value | Maximum Continuous Output Current |
| --- | --- |
| 1 to 4 | Up to 100% of inverter output current |
| 5 | Up to 90% of inverter output current |
| 6 | Up to 80% of inverter output current |

If wiring distance between inverter and motor is long, reduce the carrier frequency. For details, refer to wiring precautions on page 12.

2.7.20 FREQUENCY/CURRENT METER CALIBRATION

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| Analog Monitor Gain | 45 | 1.00 |
| Output Monitor Selection | 21 | 0000 |

Frequency/ current meter connected to the inverter can be calibrated by  without using a resistor for calibration. For the setting method, refer to Par. 2.4.2 “Calibration of Frequency Meter” on page 55 and “MULTIFUNCTION ANALOG OUTPUT MONITOR SETTING” on page 76.

Selection of output between control circuit terminals  12 -- 11

21 = X  X  0  X

2nd digit

0: Output frequency

1: Output current

2.7.21 OPERATION AT MOMENTARY POWER LOSS

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| Operation Selection after Momentary Power Loss | 46 | 0000 |
| Speed Search Operation Level | 54 | 150% |
| Minimum Baseblock Time | 55 | 0.5s |

Even if a momentary power loss occurs, operation can be continued without any problem.

46 =  X  X  X  0

1st digit

0: Continuous operation not provided after momentary power loss

1: Continuous operation provided after momentary power loss

loss

Momentary power loss assurance time differs as shown below, according to the capactiy of the models. (common to both 3-phase and single-phase series)

˙0.5 to 1HP (0.4 to 0.75Kw): Approx. 1 second

˙2 to 10HP(1.5 to 7.5Kw): Approx. 2 seconds

Note :If a power loss exceeds the momentary power loss assurance time, in the momentary power loss assurance time after the power loss, low voltage fault occurs, fault contact is output and the motor coasts to stop.

Operation when continuous operation after momentary power loss is provided , which is describing as below :

- When undervoltage(UV) is detected, the inverter output is shut off and the frequency reference value and run command given before the momentary power loss are held. Additionally, counting of the undervoltage time starts; during counting, UV is displayed, blinking on the digital display unit and digital operator. If undervoltage is detected, the inverter output is ahut off for the minimum baseblock time Pn-55.

- After recovery from the momentary power loss, after checking that the inverter DC voltage has recovered sufficiently, speed search operation is performed.

3.  Speed search operation starts when the inverter output current exceeds the speed search operation level Pn-54 set value. At this time, the new frequency reference value and run command are read in. The frequency in which the inverter output current is smaller than the speed search operation level Pn-54 set value is judged to be the speed synchronised point, and reacceleration/ redeceleration is performed up/down to the set frequency in the set accel/decel time.

Momentary power loss occurrence

Input power supply

Recover

UV detection signal

t

B.B

Motor speed

Coasting      Search  Reacceleration

1.    2.       3.

*   t :Varies according to the inverter size. (Assured at 15 mS minimum.) Operation is automatically continued if recovery from momentary power loss in   t or less.

Do not provide an excessively small value for the minimum baseblock time setting. Otherwise, the inverter protective function may operate at search operation start.(Refer to page 96.)

2.7.22  AUTOMATIC RESET AND RESTART FUNCTION

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| Fault Retry Selection | 47 | 0 |
| Speed Search Operation Level | 54 | 150% |
| Minimum Baseblock Time | 55 | 0.5s |
| V/f during Speed Search | 56 | 100% |

If an inverter fault occurs during running, the inverter performs selfdiagnosis to restart automatically.

The number of the self-diagnosis and restarting times can be set up to 10

times to 47 . By setting 0 times, the fault retry function becomes disabled.

The inverter restarts automatically in case of the following faults.

1. Overcurrent protection (OC)

2. Overvoltage protection (OV)

3. Cooling fin overheat (OH)

The number of fault retry times is cleared to 0 in the following cases:

1.No fault occurs for more than 10 minutes.

2.Fault reset input signal (or reset key on the digital operator) is turned ON when the fault is checked.

3.The power supply is turned off.

Fault retry operation is described below:

- If a fault is detected, the inverter output is shut off for the minimum baseblock time Pn-55.

While the inverter output is shut off, the fault is displayed on the digital display unit and the digital operator.

- After the minimum baseblock time Pn-55, the fault is automatically reset, and the speed search operation is performed from the output frequency at the fault occurrence.

- If the inverter output current is larger than the speed search operation level Pn-54 set value, the speed search operation starts. The frequency in which the inverter output current is smaller than the speed search operation level Pn-54 set value is judged to be the speed synchronized point, and reacceleration/ redeceleration is performed up/down to the set frequency in the set accel/decel time.

- If the total number of faults exceeds the number of retry times Pn-47, automatic reset is not performed and the inverter output is kept off. Then fault contact is output. (Fault contact is not output during fault retry.)

FAULT CONTACT IS OUTPUT.

FAULT DETECTION

FAULT CONTACT

NUMBER OF REVOLUTIONS OF MOTOR

OUTPUT FREQUENCY

Note:

1.v/f during speed search

The v/f during speed search can be set as shown below by the Pn-56 set value so that a protective function as OC will not occur during speed search. However, this setting is not needed under normal operation.

V/f during speed search=V/f at normal operation × Pn-56

2. Minimum baseblock time

Do not provide excessively small value for the minimum baseblock time setting.

Otherwise, the inverter protective function may operate at speed search operation start.

(Refer to page 96.)

2.7.23 FREQUENCY JUMP CONTROL

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| Jump Frequency 1 | 50 | 0.0Hz |
| Jump Frequency 2 | 51 | 0.0Hz |
| Jump Frequency 3 | 52 | 0.0Hz |
| Jump Width | 53 | 1.0Hz |

To operate the inverter without oscillation caused by machine system characteristic frequency, oscillation generating frequency can be allowed to jump. This function can be also for dead band control.

Pn-53 
SETTING PROHIBIT FREQUENCY RANGE

INTERNAL FREQUENCY REF.

Pn-50 
SETTING PROHIBIT FREQUENCY

Pn-51 
SETTING PROHIBIT FREQUENCY

Pn-52 
SETTING PROHIBIT FREQUENCY

SETTING FREQUENCY REF.

Constant—speed operation is prohibited within the jump width. However, output frequency does not jump during acceleration or deceleration for smooth acceleration or deceleration.

(1) Jump frequency 1 to 3 ( 50  to  52  )

By setting the value to 0.0Hz, this function becomes disabled. Set jump frequency 1 to 3 as described below :

Jump frequency 3 (52) ≦ Jump frequency 2 (51) ≦Jump frequency 1 (50)

(2) Jump width ( 53  )

By setting the value to 0.0Hz, this function becomes disabled. The range to jump is :  50 to 52 - 50 to 53 <jumping range< 50 to 52 + 50 to 53  .

(Example) When jump frequency 1 (50 ) is 45Hz and the jump width (53) is 2.0Hz: Jumping range = 43 to 47Hz.

2.7.24  SPEED SEARCH FUNCTION

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| Speed Search Function | 32 , 33 | See page |
| Speed Search Operation Level | 54 | 150% |
| Minimum Basseblock Time | 55 | 0.5s |
| V/f during Speed Search | 56 | 100% |

When the motor during coasting is started during changing operation of commercial power supply and inverter, etc., the motor can be operated without tripping by using the speed search function.

The speed search command is input from multifunction contact input terminals  4  and  5 .For the functions of terminals 4 and 5 , “9”or “10” is set to 32 or 33 .

When setting to “9”: Search from maximum frequency

When setting to “10”: Search from setting frequency

By closing the search command during baseblock and inputting the run command, speed search is started after the inverter output is shut off for the minmim baseblock time 55  .

When the inverter output current is larger than the set value of the speed search operation level 54 , the speed search operation starts. Frequency in which the inverter output current becomes smaller than the speed search operation level 54 set value is judged to be speed synchronized point, and the motor starts reacceleration/redeceleration up/down to the setting frequency in the set accel/decel time.

The following shows the time chart where the speed search command is input.

FWD (REV) RUN COMMAND

SEARCH COMMAND

MAX. FREQUENCY OR FREQUENCY REF. VALUE WHEN SEARCH COMMAND IS INPUT

AGREED SPEED DETECTION

OUTPUT FREQUENCY

MIN. BASEBLOCK TIME

VOLTAGE AT SPEED SEARCH

RETURN TO THE VOLTAGE AT NORMAL RUNNING

OUTPUT VOLTAGE

SPEED SEARCH OPERATION

Notes:

- Search commands with ser values of  9 and 10 ( e.g. Pn-32 = 9, Pn-33 = 10)

- Determine a sequence so that FWD/REV run command enters at the same time or later than search command.

RELAY 1

SEARCH COMMAND

<Example of Sequence>

RELAY 2

RELAY 1

FWD/REV RUN COMMAND

3. The minimum baseblock time is a time when the inverter output is shut off during the motor remaining voltage occurrence. Setting this time shorter can reduce the time until speed search start, but an inverter protective function such as overcurrent (OC) may operate because of the motor remaining voltage and the like. Therefore, do not reduce the time unnecessarily.

2.7.25  FREQUENCY UP/ DOWN FUNCTION

| Item Name | Constant to be set | Factory Preset |
| --- | --- | --- |
| Accel/Decel Prohibit Function | 32 , 33 | See page 63 |
| Output Frequency UP/DOWN operation | 20 | 0000 |

A) Output frequency UP/DOWN operation by control circuit terminals

When the accel/decel prohibit command is input during acceleration or deceleration, acceleration or deceleration is prohibited while the command is input, and the output frequency is held.

By inputting the stop command, the accel/decel command is released and the operation is in the stopped condition.

The accel/decel prohibit command is input from multifunction contact input terminal  4  or  5 .

For the function of terminal  4  or  5  , set all to  32  or  33

Terminal  4  function: Set to  32  .

Terminal  5  function: Set to  33  .

The following shows the time chart when the accel/decel prohibit command is input:

FWD RUN

ACCEL/DECE

PROHIBIT COMMAND

FREQUENCY REF.

OUTPUT FREQUENCY

FREQUENCY AGREED

SIGNAL

Note : Wen the FWD (REV) run command is input in the status where accel/decel prohibit command is input, the baseblock status is continued and motor does not operate.

However, when frequency reference lower limit Pn-25 ≧ minimum output frequency Pn_07 is set, the motor operates at the frequency reference lower limit Pn-25.

B) Output frequency UP/DOWN operation by digital operator key.

20  =  X  0  X  X

0: Changes the frequency reference by Increments or <

( up or down ) key, after dpress the

STR ( store ) key, then the output frequency start to

UP or DOWN.

1: The output frequency can UP or DOWN by Increment or

Decrement ( up or down )key directly, without depress

STR( store ) key. If depress the STR key, then the frequency reference set by Increment/Decrement key will be stored.

2.7.26   FUNCTIONS FOR REDUCTION OF MACHINE

VIBRATION OR SHOCK

The following constants are effective for reduction of vibration or shock.

| Effective Method | Constant to be Set | Factory Preset | Adjustment | Page |
| --- | --- | --- | --- | --- |

˙ Shock

| ˙To decrease generating torque ˙To increease generating torque | 2 to 8 | See page 59 | Decrease or increase V/f. | 59 |
| --- | --- | --- | --- | --- |
|  | 29 | 1.0 | Decrease or increase torque boost | 81 |
| To reduce shock at acceleration | 21 | 0000 | Set S-curve accel/decel. | 77 |
|  | 9 , 11 | 10.0s | Increase accel time | 71 |
|  | 30 | 170% | Increase stall prevention level during accel. | 82 |
| To reduce shock at deceleration | 1 | 0000 | Set coasting to a stop | 68 |
|  | 21 | 0000 | Set S-curve accel/decel. | 77 |
|  | 10 , 12 | 10.0s | Increase decel time | 71 |
|  | 7 | 1.5Hz | Decrease or increase minmim output frequency | 69 |
|  | 26 | 50% | Decrease DC injection braking current. | 80 |

˙Vibration

| To decrease carrier frequency | 40 | 4 | Decrease PWM carrier frequency | 89 |
| --- | --- | --- | --- | --- |

# 2.8 PROTECTION FUNCTION AND TROUBLESHOOTING

| Protection function |  | Explanation | Monitor display | Fault contact output |  |
| --- | --- | --- | --- | --- | --- |
| Low voltage protection | Main circuit low voltage | When the inverter power voltage drops, torque becomes insufficient and motor is overheated. Inverter output is stopped when the main circuit DC voltage becomes lower than the low voltage detection level. Detection level: Approximately 210 Vdc or less for 220V class 3-Phase 170 Vdc or less for 220V class single-Phase and 420 Vdc or less for 440V class 3-phase | (UV1) | Operation |  |
|  | Momentary power loss protection |  |  |  |  |
| Overcurrent protection |  | The inverter output is shut-off when the inverter output current becomes approx. 200% and above of inverter rated current. | (OC) | Operation |  |
| Ground - fault protection (Optional function) |  | The inverter out is shut-off when a ground-fault occurs at the inverter output side and the ground-fault current exceeds approximately 50% of the inverter rated current. |  | Operation |  |
| Overvoltage protection |  | The inverter output is shut-off when the main circuit DC voltage becomes excessive because of regeneration energy caused by motor deceleration and negative load. Detection: Approx. 820 Vdc or more for input voltage 440V class 410 Vdc or more for input voltage 220V class | (OV) | Operation |  |
| Fuse blown |  | The inverter output is shut-off when the main circuit transistor fails. The fuse clears to prevent wiring from being by the short-circuit current. | Not display | No Operation |  |
| Cooling fin overheat (Only for forced cooling type) |  | The inverter output is shut-off when the ambient temperature rises and the heat sink fin reaches 90 ℃. Please check for a defective cooling fan or clogged filter. | (OH) | Operation |  |
| Overload protection | Motor | Inverter output is stopped when motor overload is detected by the electronic thermal overload in the inverter. Either a inverter duty constant-torque specialized motor or general-purpose motor can be selected. If more than one motor is driven, overload protection should be disabled. Use a thermal relay or thermal protector for each motor. | (OL1) | Operation |  |
|  | Inverter | The inverter output is shut-off when the electronic thermal overload reaches or exceeds the inverse time limit of 112% of the inverter's rated current occurs. Maximum rated overload: 150%, 1 min. | (OL2) | Operation |  |
|  | Over torque detection *1 | The motor operates according to a preset mode when the inverter output current exceeds the overtorque detection level. This function is used to protect the machine or to monitor the output torque. | (OL3) | Operation |  |
| External fault signal input |  | When an external alarm signal is input, the inverter operates according to a preset stop method (coasting to a stop, continuous operation, or ramp to stop) | EF4 to EF5 | Operation |  |
| Control circuit fault, option fault *2 |  | The inverter output is shut-off when a transmission error occurs in the control circuit or a component fails. The inverter output is also shut-off when a specialized option such as the digital operator is not properly connected. | To | Operation |  |

*1. For overtorque detection (OL3), fault display or alarm display can be selected according to the constant (Pn-37) setting. For details refer to “Overtorque Detection Function” on page 88.

*2. For details of control circuit faults, refer to Table 1.9 “Details of CPF Display” on page 29 indicate the contents of digital operator display.

|  | Error causes | Action to be taken |
| --- | --- | --- |
| Uv1 OC | - Inverter capacity is too small. - Voltage drop due to wiring. - Inverter power voltage selection is wrong. - A motor of large capacity (11 kW or greater) connected to the same power system has been started. - Rapid acceleration with generator power supply - Operation sequence when power is off - Defective electromagnetic contactor | - Check the power capacity and power system. - UV display appears when the inverter power is turned off while operation signal is input. Remove the power after stopping the inverter. (Set the third and fourth bits of Sn-04 to 01.) |
|  | - Extremely rapid accel/decel - Motor on/off switching at the inverter output side - Short-circuit or ground-fault at the inverter output side - Motor of a capacity greater than the inverter rating has been started - High-speed motor or pulse motor has been started. | Transistor error may occur. Investigate the error cause, correct it, then restart. |
| GF | - Motor dielectric strength is insufficient. - Load wiring is not proper. | Check for ground-fault in motor or load wiring. |
| OV | - Over voltage - Insufficient deceleration time - Regenerative load (Motor is turned by the load.) - High input voltage compared to motor rated voltage | If braking torque is not proper, extend the decel time or use a braking resistor. (If braking resistor is already installed, verify that Sn-10, 2nd digit to 1.) |
| FU | - Repeated overcurrent protection (OC) - Repeated overload protection (OL2) power reset - Rapid deceleration in excess excitation (improper V/f characteristic setting) - External noise | Correct the cause, check the main circuit transistor, replace the fuse, then restart. |
| OH | - Defective cooling fan - Ambient temperature rise - Clogged filter | Replace the cooling fan and clean the filter. Ambient temperature: 104 ℉ (40 ℃) or less for enclosed type 122 ℉ (50 ℃) or less for open chassis |
| OL1 OL2 | Overload, low speed operation or extended acceleration time, improper V/f characteristic setting. Motor rated current (Pn-19) setting is wrong. | Investigate the cause of overload and review the operation pattern, V/f characteristic, and motor/inverter capacities. (If inverter is repeatedly reset after an overload occurs, the inverter may fault. Investigate and correct the cause of overload.) |
| OL3 | Motor Current exceeds the preset value because of machine error or overload. | Check the use of the machine. Correct the overload cause or set a higher detection level which is within the allowable range. |
| EF4 EF5 | External fault condition occurred. | Correct the cause of the fault input. |
|  | - External noise - Excess vibration or shock - CPF 02: Control circuit fault - CPF 03: NVRAM (SRAM) fault - CPF 04: NVRAM BCC Code error - CPF 05: AD converter fault in CPU | - Check data in parameter setting. Record all data, then set Pn-00 = 08 for initializing. - Turn off power, then turn on again. If error is persistent, contact your TECO representative. |

2.9 Warning and Self-Diagnosis Functions

| Protection function |  | Explanation | Monitor display | Fault contact output |  |
| --- | --- | --- | --- | --- | --- |
| Low-voltage protection main circuit voltage insufficient |  | Monitor display appears if low voltage protection conditions such as a drop in main circuit voltage or momentary power loss occur while the inverter output is off. | (UV) (Blink) | Non operation |  |
| Over voltage protection |  | Monitor display appears when the main circuit DC voltage rises above the detection level while the inverter output is off. | (OV) (Blink) | Non operation |  |
| Cooling fin overheat warning |  | Monitor display appears when a separate thermal protector contact is input to the external terminal. | (OH) (Blink) | Non operation |  |
| Overtorque detection |  | This function is used to protect the machine and to monitor the inverter output torque. The inverter output reacts in a preset manner when the inverter output current exceeds the over torque detection level. The monitor display blinks when "operation continue" is preset. | (OL3) (Blink) | Non operation |  |
| Stall prevention Accel/decel is accomplished with maximum capacity of the inverter without trip- ping on over- current or overvoltage a | During acceleration | Inverter acceleration is stopped when 170% of or more of the inverter rated current is required by the load. This prevents overload protection (OL2) or overcurrent (OC) from occurring. When current is reduced to less than 170%, acceleration is enabled. | － | Non operation |  |
|  | During normal operation | Output frequency is decreased when 160% of the inverter rated current or greater is required by the load. This prevents motor and inverter overload (OL1, OL2). When current is reduced below 160%, inverter acceleration is than enabled. |  |  |  |
|  | During deceleration | Deceleration is stopped when the DC voltage is caused to rise by motor regenerative energy. This prevents overvoltage trips (OV). When DC voltage decreases, deceleration to the set value then resumes. |  |  |  |
| Simultaneous normal and reverse rotation commands |  | When forward and reverse rotation commands are simultaneously detected for a period of time exceeding 500ms, the inverter is stopped according to the preset stop method. | (EF) (Blink) | Non operation |  |
| External baseblock signal input (Minor failure) main circuit transistor instantaneous shut-off |  | When an external base block signal is input, the motor coasts to a stop. When the external base block signal is removed, the inverter output is immediately turned on at the previously set frequency. | (BB) (Blink) | Non operation |  |
| Digital operator communication error |  | Digital operator communication error 1 |  | Non operation |  |
|  |  | Digital operator communication error 2 |  |  |  |

|  | Error causes | Action to be taken |
| --- | --- | --- |
| UV | - Input voltage drop | Check the main circuit DC voltage in Un-xx. If the voltage is low, adjust the input voltage. |
| OV | - Input voltage rise | Check the main circuit DC voltage in Un-xx. If the voltage is high, adjust the input voltage. |
| OH | - Overload - Cooling fan fault - Ambient temperature rise - Clogged filter | Replace the cooling fan and clean the filter. Ambient temperature: 104℉ (40℃) or less for enclosed type 122℉ (50℃) or less for open chassis |
| OL3 | - Motor current exceeded the set value because of machine fault or overload. | Check the driven machine and correct the cause of the fault or set to a higher value. |
| STALL | - Insufficient power for accel/decel - Overload - Phase loss | - Set proper accel/decel time for smooth operation. - For stall prevention during normal operation lighten the load or increase inverter capacity. |
| EF | - Operation sequence error - 3-wire/2-wire selection error | - Recheck the control sequence. - Recheck system constant (Pn-32 to Pn -33). |
| bb | - External fault conditions set-up | Take appropriate measurement for the cause of external fault input. |
| CPF00 CPF02 | - External noise - Excess Vibration or shock - Digital operator fault - Control board fault | - Check the digital operator connection - Turn off the power supply once and turn it on again. If the fault still exists, replace the digital operator or control board. |